## FromPLC
NVPP
Interfacelist with signals that Aquasuite reads from PLC
BJ2002
Version 1.1 11/06/2024
Aquasuite signals FromPLC | DataType | Scale | Bit | Address/ register | Bit rack | Freeze signal | Description | Unit of Meas | Range Min | Range Max | Delta | Aggregate | Remarks client | Remarks RHDHV | EAE_OPCUA_TAG
Aeration.Equipment.Blower01.Alarm | Boolean |  |  |  |  | x | Aeration Blower 1 (MOD NVPP 001 bl-- 001) Alarm | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor1.Blower1.feedbackFailure.IThis.AlarmStatus
Aeration.Equipment.Blower01.Capacity | Float |  |  |  |  | x | Aeration Blower 1 (MOD NVPP 001 bl-- 001) Capacity | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor1.Blower1.IThis.SpeedSp
Aeration.Equipment.Blower01.Frequency | Float |  |  |  |  | x | Aeration Blower 1 (MOD NVPP 001 bl-- 001) Frequency | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor1.Blower1.IThis.SpeedPv
Aeration.Equipment.Blower01.Mode | Boolean |  |  |  |  | x | Aeration Blower 1 (MOD NVPP 001 bl-- 001) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor1.Blower1.IThis.Mode
Aeration.Equipment.Blower01.Power | Float |  |  |  |  | x | Aeration Blower 1 (MOD NVPP 001 bl-- 001) Power (kW)
Aeration.Equipment.Blower01.Run | Boolean |  |  |  |  | x | Aeration Blower 1 (MOD NVPP 001 bl-- 001) Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor1.Blower1.IThis.CurrentOp
Aeration.Equipment.Blower02.Alarm | Boolean |  |  |  |  | x | Aeration Blower 2 (MOD NVPP 001 bl-- 002) Alarm | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor1.Blower2.feedbackFailure.IThis.AlarmStatus
Aeration.Equipment.Blower02.Capacity | Float |  |  |  |  | x | Aeration Blower 2 (MOD NVPP 001 bl-- 002) Capacity | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor1.Blower2.IThis.SpeedSp
Aeration.Equipment.Blower02.Frequency | Float |  |  |  |  | x | Aeration Blower 2 (MOD NVPP 001 bl-- 002) Frequency | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor1.Blower2.IThis.SpeedPv
Aeration.Equipment.Blower02.Mode | Boolean |  |  |  |  | x | Aeration Blower 2 (MOD NVPP 001 bl-- 002) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor1.Blower2.IThis.Mode
Aeration.Equipment.Blower02.Power | Float |  |  |  |  | x | Aeration Blower 2 (MOD NVPP 001 bl-- 002) Power (kW)
Aeration.Equipment.Blower02.Run | Boolean |  |  |  |  | x | Aeration Blower 2 (MOD NVPP 001 bl-- 002) Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor1.Blower2.IThis.CurrentOp
Aeration.Equipment.Blower03.Alarm | Boolean |  |  |  |  | x | Aeration Blower 3 (MOD NVPP 001 bl-- 003) Alarm | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor2.Blower1.feedbackFailure.IThis.AlarmStatus
Aeration.Equipment.Blower03.Capacity | Float |  |  |  |  | x | Aeration Blower 3 (MOD NVPP 001 bl-- 003) Capacity | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor2.Blower1.IThis.SpeedSp
Aeration.Equipment.Blower03.Frequency | Float |  |  |  |  | x | Aeration Blower 3 (MOD NVPP 001 bl-- 003) Frequency | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor2.Blower1.IThis.SpeedPv
Aeration.Equipment.Blower03.Mode | Boolean |  |  |  |  | x | Aeration Blower 3 (MOD NVPP 001 bl-- 003) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor2.Blower1.IThis.Mode
Aeration.Equipment.Blower03.Power | Float |  |  |  |  | x | Aeration Blower 3 (MOD NVPP 001 bl-- 003) Power (kW)
Aeration.Equipment.Blower03.Run | Boolean |  |  |  |  | x | Aeration Blower 3 (MOD NVPP 001 bl-- 003) Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor2.Blower1.IThis.CurrentOp
Aeration.Equipment.Blower04.Alarm | Boolean |  |  |  |  | x | Aeration Blower 4 (MOD NVPP 001 bl-- 004) Alarm | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor2.Blower2.feedbackFailure.IThis.AlarmStatus
Aeration.Equipment.Blower04.Capacity | Float |  |  |  |  | x | Aeration Blower 4 (MOD NVPP 001 bl-- 004) Capacity | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor2.Blower2.IThis.SpeedSp
Aeration.Equipment.Blower04.Frequency | Float |  |  |  |  | x | Aeration Blower 4 (MOD NVPP 001 bl-- 004) Frequency | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor2.Blower2.IThis.SpeedPv
Aeration.Equipment.Blower04.Mode | Boolean |  |  |  |  | x | Aeration Blower 4 (MOD NVPP 001 bl-- 004) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor2.Blower2.IThis.Mode
Aeration.Equipment.Blower04.Power | Float |  |  |  |  | x | Aeration Blower 4 (MOD NVPP 001 bl-- 004) Power (kW)
Aeration.Equipment.Blower04.Run | Boolean |  |  |  |  | x | Aeration Blower 4 (MOD NVPP 001 bl-- 004) Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor2.Blower2.IThis.CurrentOp
Aeration.Equipment.Blower05.Alarm | Boolean |  |  |  |  | x | Aeration Blower 5 (MOD NVPP 001 bl-- 005) Alarm | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor3.Blower1.feedbackFailure.IThis.AlarmStatus
Aeration.Equipment.Blower05.Capacity | Float |  |  |  |  | x | Aeration Blower 5 (MOD NVPP 001 bl-- 005) Capacity | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor3.Blower1.IThis.SpeedSp
Aeration.Equipment.Blower05.Frequency | Float |  |  |  |  | x | Aeration Blower 5 (MOD NVPP 001 bl-- 005) Frequency | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor3.Blower1.IThis.SpeedPv
Aeration.Equipment.Blower05.Mode | Boolean |  |  |  |  | x | Aeration Blower 5 (MOD NVPP 001 bl-- 005) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor3.Blower1.IThis.Mode
Aeration.Equipment.Blower05.Power | Float |  |  |  |  | x | Aeration Blower 5 (MOD NVPP 001 bl-- 005) Power (kW)
Aeration.Equipment.Blower05.Run | Boolean |  |  |  |  | x | Aeration Blower 5 (MOD NVPP 001 bl-- 005) Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor3.Blower1.IThis.CurrentOp
Aeration.Equipment.Blower06.Alarm | Boolean |  |  |  |  | x | Aeration Blower 6 (MOD NVPP 001 bl-- 006) Alarm | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor3.Blower2.feedbackFailure.IThis.AlarmStatus
Aeration.Equipment.Blower06.Capacity | Float |  |  |  |  | x | Aeration Blower 6 (MOD NVPP 001 bl-- 006) Capacity | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor3.Blower2.IThis.SpeedSp
Aeration.Equipment.Blower06.Frequency | Float |  |  |  |  | x | Aeration Blower 6 (MOD NVPP 001 bl-- 006) Frequency | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor3.Blower2.IThis.SpeedPv
Aeration.Equipment.Blower06.Mode | Boolean |  |  |  |  | x | Aeration Blower 6 (MOD NVPP 001 bl-- 006) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor3.Blower2.IThis.Mode
Aeration.Equipment.Blower06.Power | Float |  |  |  |  | x | Aeration Blower 6 (MOD NVPP 001 bl-- 006) Power (kW)
Aeration.Equipment.Blower06.Run | Boolean |  |  |  |  | x | Aeration Blower 6 (MOD NVPP 001 bl-- 006) Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor3.Blower2.IThis.CurrentOp
Aeration.Equipment.Ventilator01.Alarm | Boolean |  |  |  |  | x | Aeration Ventilator 1 (MOD NVPP 001 VAN 002) Alarm
Aeration.Equipment.Ventilator01.Mode | Boolean |  |  |  |  | x | Aeration Ventilator 1 (MOD NVPP 001 VAN 002) Mode from SCADA (0=Manual, 1=Auto)
Aeration.Equipment.Ventilator01.Run | Boolean |  |  |  |  | x | Aeration Ventilator 1 (MOD NVPP 001 VAN 002) Status Run
Aeration.Equipment.Ventilator02.Alarm | Boolean |  |  |  |  | x | Aeration Ventilator 2 (MOD NVPP 001 VAN 003) Alarm
Aeration.Equipment.Ventilator02.Mode | Boolean |  |  |  |  | x | Aeration Ventilator 2 (MOD NVPP 001 VAN 003) Mode from SCADA (0=Manual, 1=Auto)
Aeration.Equipment.Ventilator02.Run | Boolean |  |  |  |  | x | Aeration Ventilator 2 (MOD NVPP 001 VAN 003) Status Run
Aeration.Signal.Pressure01 | Float |  |  |  |  | x | Aeration Pressure indicator blower 1 (MOD NVPP 001 PI 006) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor1.Sensor.NVPP_001_PI_00X_1.IThis.Pv
Aeration.Signal.Pressure02 | Float |  |  |  |  | x | Aeration Pressure indicator blower 2 (MOD NVPP 001 PI 007) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor1.Sensor.NVPP_001_PI_00X_2.IThis.Pv
Aeration.Signal.Pressure03 | Float |  |  |  |  | x | Aeration Pressure indicator blower 3 (MOD NVPP 001 PI 008) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor2.Sensor.NVPP_001_PI_00X_1.IThis.Pv
Aeration.Signal.Pressure04 | Float |  |  |  |  | x | Aeration Pressure indicator blower 4 (MOD NVPP 001 PI 009) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor2.Sensor.NVPP_001_PI_00X_2.IThis.Pv
Aeration.Signal.Pressure05 | Float |  |  |  |  | x | Aeration Pressure indicator blower 5 (MOD NVPP 001 PI 010) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor3.Sensor.NVPP_001_PI_00X_1.IThis.Pv
Aeration.Signal.Pressure06 | Float |  |  |  |  | x | Aeration Pressure indicator blower 6 (MOD NVPP 001 PI 011) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_AerationReactor3.Sensor.NVPP_001_PI_00X_2.IThis.Pv
Chemicals.Equipment.ChemicalsDosingValve.Alarm | Boolean |  |  |  |  | x | Chemicals Feed buffer chemicals dosing valve, Alarm status (MOD NVPP 001 a-- 058) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.NVPP_001_a_058.Valve.feedbackFailure.IThis.AlarmStatus
Chemicals.Equipment.ChemicalsDosingValve.Closed | Boolean |  |  |  |  | x | Chemicals Feed buffer chemicals dosing valve, Closed status (MOD NVPP 001 a-- 058) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.NVPP_001_a_058.IThis.FbClosed
Chemicals.Equipment.ChemicalsDosingValve.Mode | Boolean |  |  |  |  | x | Chemicals Feed buffer chemicals dosing valve (MOD NVPP 001 a-- 058) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.NVPP_001_a_058.Valve.IThis.Mode
Chemicals.Equipment.ChemicalsDosingValve.Open | Boolean |  |  |  |  | x | Chemicals Feed buffer chemicals dosing valve, Open status (MOD NVPP 001 a-- 058) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.NVPP_001_a_058.IThis.FbOpen
Chemicals.Equipment.DosingPump.Alarm | Boolean |  |  |  |  | x | Chemicals Chemical dosing pump (MOD NVPP 001 FDO 001) Alarm | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.MetalSaldDosingPump.NVPP_001_fdp_002.feedbackFailure.IThis.AlarmStatus
Chemicals.Equipment.DosingPump.Mode | Boolean |  |  |  |  | x | Chemicals Chemical dosing pump (MOD NVPP 001 FDO 001) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.MetalSaldDosingPump.NVPP_001_fdp_002.IThis.Mode
Chemicals.Equipment.DosingPump.Power | Float |  |  |  |  | x | Chemicals Chemical dosing pump (MOD NVPP 001 FDO 001) Power (kW)
Chemicals.Equipment.DosingPump.Run | Boolean |  |  |  |  | x | Chemicals Chemical dosing pump (MOD NVPP 001 FDO 001) Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.MetalSaldDosingPump.NVPP_001_fdp_002.IThis.CurrentOp
Effluent.Equipment.BackwashWaterValve.Alarm | Boolean |  |  |  |  | x | Effluent Backwash valve (when closed water can be used for flushing), Alarm status (MOD NVPP 001 a-- 014) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_014.Valve.feedbackFailure.IThis.AlarmStatus
Effluent.Equipment.BackwashWaterValve.Closed | Boolean |  |  |  |  | x | Effluent Backwash valve (when closed water can be used for flushing), Closed status (MOD NVPP 001 a-- 014) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_014.IThis.FbClosed
Effluent.Equipment.BackwashWaterValve.Mode | Boolean |  |  |  |  | x | Effluent Backwash valve (when closed water can be used for flushing) (MOD NVPP 001 a-- 014) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_014.Valve.IThis.Mode
Effluent.Equipment.BackwashWaterValve.Open | Boolean |  |  |  |  | x | Effluent Backwash valve (when closed water can be used for flushing), Open status (MOD NVPP 001 a-- 014) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_014.IThis.FbOpen
Effluent.Equipment.DischargeValve.Alarm | Boolean |  |  |  |  | x | Effluent Effluent buffer discharge valve, Alarm status (MOD NVPP 001 a-- 011) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_011.Valve.feedbackFailure.IThis.AlarmStatus
Effluent.Equipment.DischargeValve.Closed | Boolean |  |  |  |  | x | Effluent Effluent buffer discharge valve, Closed status (MOD NVPP 001 a-- 011) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_011.IThis.FbClosed
Effluent.Equipment.DischargeValve.Mode | Boolean |  |  |  |  | x | Effluent Effluent buffer discharge valve (MOD NVPP 001 a-- 011) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_011.Valve.IThis.Mode
Effluent.Equipment.DischargeValve.Open | Boolean |  |  |  |  | x | Effluent Effluent buffer discharge valve, Open status (MOD NVPP 001 a-- 011) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_011.IThis.FbOpen
Effluent.Equipment.DrainValve.Alarm | Boolean |  |  |  |  | x | Effluent Effluent discharge drain valve, Alarm status (46 2 AP a-- 95 009) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_46_2_AP_a_95_009.Valve.feedbackFailure.IThis.AlarmStatus
Effluent.Equipment.DrainValve.Closed | Boolean |  |  |  |  | x | Effluent Effluent discharge drain valve, Closed status (46 2 AP a-- 95 009) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_46_2_AP_a_95_009.IThis.FbClosed
Effluent.Equipment.DrainValve.Mode | Boolean |  |  |  |  | x | Effluent Effluent discharge drain valve (46 2 AP a-- 95 009) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_46_2_AP_a_95_009.Valve.IThis.Mode
Effluent.Equipment.DrainValve.Open | Boolean |  |  |  |  | x | Effluent Effluent discharge drain valve, Open status (46 2 AP a-- 95 009) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_46_2_AP_a_95_009.IThis.FbOpen
Effluent.Equipment.Pump.Alarm | Boolean |  |  |  |  | x | Effluent Effluent pump (MOD NVPP 001 CTP 002) Alarm | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_ctp_002.feedbackFailure.IThis.AlarmStatus
Effluent.Equipment.Pump.Capacity | Float |  |  |  |  | x | Effluent Effluent pump (MOD NVPP 001 CTP 002) Capacity | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_ctp_002.IThis.SpeedSp
Effluent.Equipment.Pump.Frequency | Float |  |  |  |  | x | Effluent Effluent pump (MOD NVPP 001 CTP 002) Frequency | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_ctp_002.IThis.SpeedPv
Effluent.Equipment.Pump.Mode | Boolean |  |  |  |  | x | Effluent Effluent pump (MOD NVPP 001 CTP 002) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_ctp_002.IThis.Mode
Effluent.Equipment.Pump.Power | Float |  |  |  |  | x | Effluent Effluent pump (MOD NVPP 001 CTP 002) Power (kW)
Effluent.Equipment.Pump.Run | Boolean |  |  |  |  | x | Effluent Effluent pump (MOD NVPP 001 CTP 002) Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_ctp_002.IThis.CurrentOp
Effluent.Signal.Flow | Float |  |  |  |  | x | Effluent Effluent flow measurement (MOD NVPP 001 FT 002) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_ft_002.IThis.Pv
Effluent.Signal.Flow.Alarm | Boolean |  |  |  |  | x | Effluent Effluent flow measurement Alarm (MOD NVPP 001 FT 002) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_ft_002.signalConditioning.ChFailureAlarm.IThis.AlarmStatus
Effluent.Signal.Level | Float |  |  |  |  | x | Effluent Effluent buffer level measurement (MOD NVPP 001 LT 002) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_lt_002.IThis.Pv
Effluent.Signal.Level.Alarm | Boolean |  |  |  |  | x | Effluent Effluent buffer level measurement Alarm (MOD NVPP 001 LT 002) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_lt_002.signalConditioning.ChFailureAlarm.IThis.AlarmStatus
Effluent.Signal.NH4 | Float |  |  |  |  | x | Effluent Ammonia measurement (MOD NVPP 001 40QT2104) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2104.IThis.Pv
Effluent.Signal.NH4.Calibrating | Boolean |  |  |  |  | x | Effluent Ammonia measurement Calibrating bit from 16-bit analyzer status word, Bit 0 (MOD NVPP 001 40QT2104) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2104_Status.IThis.Calibrating
Effluent.Signal.NH4.Cleaning | Boolean |  |  |  |  | x | Effluent Ammonia measurement Cleaning bit from 16-bit analyzer status word, Bit 1 (MOD NVPP 001 40QT2104) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2104_Status.IThis.Cleaning
Effluent.Signal.NH4.CommonError | Boolean |  |  |  |  | x | Effluent Ammonia measurement CommonError bit from 16-bit analyzer status word, bit 3 (MOD NVPP 001 40QT2104) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2104_Status.IThis.CommonError
Effluent.Signal.NH4.DaysToMaintenance | Integer |  |  |  |  | x | Effluent Ammonia measurement DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (MOD NVPP 001 40QT2104) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2104_Status.IThis.DaysToMaintenance
Effluent.Signal.NH4.Reliability | Integer |  |  |  |  | x | Effluent Ammonia measurement Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (MOD NVPP 001 40QT2104) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2104_Status.IThis.Reliability
Effluent.Signal.NH4.Service | Boolean |  |  |  |  | x | Effluent Ammonia measurement Service bit from 16-bit analyzer status word, Bit 2 (MOD NVPP 001 40QT2104) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2104_Status.IThis._Service
Effluent.Signal.NO3 | Float |  |  |  |  | x | Effluent Nitrate measurement (MOD NVPP 001 40QT2105) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2105.IThis.Pv
Effluent.Signal.NO3.CommonError | Boolean |  |  |  |  | x | Effluent Nitrate measurement CommonError bit from 16-bit analyzer status word, bit 3 (MOD NVPP 001 40QT2105) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2105_Status.IThis.CommonError
Effluent.Signal.NO3.DaysToMaintenance | Integer |  |  |  |  | x | Effluent Nitrate measurement DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (MOD NVPP 001 40QT2105) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2105_Status.IThis.DaysToMaintenance
Effluent.Signal.NO3.Reliability | Integer |  |  |  |  | x | Effluent Nitrate measurement Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (MOD NVPP 001 40QT2105) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2105_Status.IThis.Reliability
Effluent.Signal.PO4 | Float |  |  |  |  | x | Effluent Phosphate analyser (MOD NVPP 001 40QT2102) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2102.IThis.Pv
Effluent.Signal.PO4.Calibrating | Boolean |  |  |  |  | x | Effluent Phosphate analyser Calibrating bit from 16-bit analyzer status word, Bit 0 (MOD NVPP 001 40QT2102) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2102_Status.IThis.Calibrating
Effluent.Signal.PO4.Cleaning | Boolean |  |  |  |  | x | Effluent Phosphate analyser Cleaning bit from 16-bit analyzer status word, Bit 1 (MOD NVPP 001 40QT2102) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2102_Status.IThis.Cleaning
Effluent.Signal.PO4.CommonError | Boolean |  |  |  |  | x | Effluent Phosphate analyser CommonError bit from 16-bit analyzer status word, bit 3 (MOD NVPP 001 40QT2102) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2102_Status.IThis.CommonError
Effluent.Signal.PO4.DaysToMaintenance | Integer |  |  |  |  | x | Effluent Phosphate analyser DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (MOD NVPP 001 40QT2102) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2102_Status.IThis.DaysToMaintenance
Effluent.Signal.PO4.Reliability | Integer |  |  |  |  | x | Effluent Phosphate analyser Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (MOD NVPP 001 40QT2102) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2102_Status.IThis.Reliability
Effluent.Signal.PO4.Service | Boolean |  |  |  |  | x | Effluent Phosphate analyser Service bit from 16-bit analyzer status word, Bit 2 (MOD NVPP 001 40QT2102) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2102_Status.IThis._Service
Effluent.Signal.Turbidity | Float |  |  |  |  | x | Effluent Turbidity measurement (MOD NVPP 001 40QT2101) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2101.IThis.Pv
Effluent.Signal.Turbidity.CommonError | Boolean |  |  |  |  | x | Effluent Turbidity measurement CommonError bit from 16-bit analyzer status word, bit 3 (MOD NVPP 001 40QT2101) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2101_Status.IThis.CommonError
Effluent.Signal.Turbidity.DaysToMaintenance | Integer |  |  |  |  | x | Effluent Turbidity measurement DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (MOD NVPP 001 40QT2101) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2101_Status.IThis.DaysToMaintenance
Effluent.Signal.Turbidity.Reliability | Integer |  |  |  |  | x | Effluent Turbidity measurement Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (MOD NVPP 001 40QT2101) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_001_40QT2101_Status.IThis.Reliability
Energy.Signal.Power | Float |  |  |  |  | x | Energy Total power usage of NVPP (??) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.MCCPower.IThis.MCCPower
FeedBuffer.Compartment.Signal.Level | Float |  |  |  |  | x | Compartment Feed buffer level measurement (MOD NVPP 001 LT 001) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.Sensor.NVPP_001_lt_001.IThis.Pv
FeedBuffer.Compartment.Signal.Level.Alarm | Boolean |  |  |  |  | x | Compartment Feed buffer level measurement Alarm (MOD NVPP 001 LT 001) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.Sensor.NVPP_001_lt_001.signalConditioning.ChFailureAlarm.IThis.AlarmStatus
FeedBuffer.Equipment.Mixer.Alarm | Boolean |  |  |  |  | x | FeedBuffer Feed buffer mixer (MOD NVPP 001 MNG 001) Alarm | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_001_mng_001.Mixer.feedbackFailure.IThis.AlarmStatus
FeedBuffer.Equipment.Mixer.Mode | Boolean |  |  |  |  | x | FeedBuffer Feed buffer mixer (MOD NVPP 001 MNG 001) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_001_mng_001.Mixer.IThis.Mode
FeedBuffer.Equipment.Mixer.Power | Float |  |  |  |  | x | FeedBuffer Feed buffer mixer (MOD NVPP 001 MNG 001) Power (kW)
FeedBuffer.Equipment.Mixer.Run | Boolean |  |  |  |  | x | FeedBuffer Feed buffer mixer (MOD NVPP 001 MNG 001) Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_001_mng_001.Mixer.IThis.CurrentOp
FeedBuffer.Equipment.PumpValve.Alarm | Boolean |  |  |  |  | x | FeedBuffer Reactors feed pump valve, Alarm status (MOD NVPP 001 a-- 003) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_001_a_003.Valve.feedbackFailure.IThis.AlarmStatus
FeedBuffer.Equipment.PumpValve.Closed | Boolean |  |  |  |  | x | FeedBuffer Reactors feed pump valve, Closed status (MOD NVPP 001 a-- 003) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_001_a_003.IThis.FbClosed
FeedBuffer.Equipment.PumpValve.Mode | Boolean |  |  |  |  | x | FeedBuffer Reactors feed pump valve (MOD NVPP 001 a-- 003) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_001_a_003.Valve.IThis.Mode
FeedBuffer.Equipment.PumpValve.Open | Boolean |  |  |  |  | x | FeedBuffer Reactors feed pump valve, Open status (MOD NVPP 001 a-- 003) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_001_a_003.IThis.FbOpen
FeedBuffer.Equipment.ReactorFeedPump.Alarm | Boolean |  |  |  |  | x | FeedBuffer Reactors feed pump (MOD NVPP 001 CTP 001) Alarm | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_001_ctp_001.feedbackFailure.IThis.AlarmStatus
FeedBuffer.Equipment.ReactorFeedPump.Capacity | Float |  |  |  |  | x | FeedBuffer Reactors feed pump (MOD NVPP 001 CTP 001) Capacity | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_001_ctp_001.IThis.SpeedSp
FeedBuffer.Equipment.ReactorFeedPump.Frequency | Float |  |  |  |  | x | FeedBuffer Reactors feed pump (MOD NVPP 001 CTP 001) Frequency | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_001_ctp_001.IThis.SpeedPv
FeedBuffer.Equipment.ReactorFeedPump.Mode | Boolean |  |  |  |  | x | FeedBuffer Reactors feed pump (MOD NVPP 001 CTP 001) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_001_ctp_001.IThis.Mode
FeedBuffer.Equipment.ReactorFeedPump.Power | Float |  |  |  |  | x | FeedBuffer Reactors feed pump (MOD NVPP 001 CTP 001) Power (kW)
FeedBuffer.Equipment.ReactorFeedPump.Run | Boolean |  |  |  |  | x | FeedBuffer Reactors feed pump (MOD NVPP 001 CTP 001) Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_001_ctp_001.IThis.CurrentOp
FeedBuffer.Phase.FB_MetalDosing.OperatingConditionsFailed | Integer |  |  |  |  | x | FeedBuffer Phase MetalDosing Operating Conditions Failed | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.MetalSaltDosinglogic.OCMetalSaltDosing.IThis.OC_Statusword
FeedBuffer.Phase.FB_MetalDosing.Status.Aborted | Boolean |  |  |  |  | x | FeedBuffer Phase MetalDosing Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.MetalSaltDosinglogic.PhaseMetalSaltDosing.Command.ABORTED
FeedBuffer.Phase.FB_MetalDosing.Status.Aborting | Boolean |  |  |  |  | x | FeedBuffer Phase MetalDosing Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.MetalSaltDosinglogic.PhaseMetalSaltDosing.Command.ABORTING
FeedBuffer.Phase.FB_MetalDosing.Status.Interlocked | Boolean |  |  |  |  | x | FeedBuffer Phase MetalDosing Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.MetalSaltDosinglogic.PhaseMetalSaltDosing.Command.INTERLOCKED
FeedBuffer.Phase.FB_MetalDosing.Status.Ready | Boolean |  |  |  |  | x | FeedBuffer Phase MetalDosing Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.MetalSaltDosinglogic.PhaseMetalSaltDosing.Command.READY
FeedBuffer.Phase.FB_MetalDosing.Status.Run | Boolean |  |  |  |  | x | FeedBuffer Phase MetalDosing Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.MetalSaltDosinglogic.PhaseMetalSaltDosing.Command.RUN
FeedBuffer.Phase.FB_MetalDosing.Status.Starting | Boolean |  |  |  |  | x | FeedBuffer Phase MetalDosing Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.MetalSaltDosinglogic.PhaseMetalSaltDosing.Command.STARTING
FeedBuffer.Phase.FB_MetalDosing.Status.Stopping | Boolean |  |  |  |  | x | FeedBuffer Phase MetalDosing Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.MetalSaltDosinglogic.PhaseMetalSaltDosing.Command.STOPPING
FeedBuffer.Signal.FlowOut | Float |  |  |  |  | x | FeedBuffer Feed buffer flow out (MOD NVPP 001 FT 001) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.Sensor.NVPP_001_ft_001.IThis.Pv
FeedBuffer.Signal.FlowOut.Alarm | Boolean |  |  |  |  | x | FeedBuffer Feed buffer flow out Alarm (MOD NVPP 001 FT 001) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.Sensor.NVPP_001_ft_001.signalConditioning.ChFailureAlarm.IThis.AlarmStatus
HeartBeat | Boolean | [5 empty] | Heartbeat signal from PLC to Nereda Controller | [7 empty] | SoftdPAC_BX1_NVPP.RES0.HeartBeat.IThis_ForOPCUA.HeartBeat_PLC_to_Nereda
Influent.Equipment.DrainValve.Alarm | Boolean |  |  |  |  | x | Influent Influent pipe drain valve, Alarm status (46 2 AP a-- 95 003) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_46_2_AP_a_95_003.Valve.feedbackFailure.IThis.AlarmStatus
Influent.Equipment.DrainValve.Closed | Boolean |  |  |  |  | x | Influent Influent pipe drain valve, Closed status (46 2 AP a-- 95 003) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_46_2_AP_a_95_003.IThis.FbClosed
Influent.Equipment.DrainValve.Mode | Boolean |  |  |  |  | x | Influent Influent pipe drain valve (46 2 AP a-- 95 003) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_46_2_AP_a_95_003.Valve.IThis.Mode
Influent.Equipment.DrainValve.Open | Boolean |  |  |  |  | x | Influent Influent pipe drain valve, Open status (46 2 AP a-- 95 003) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_46_2_AP_a_95_003.IThis.FbOpen
Influent.Equipment.InfluentPump.Alarm | Boolean |  |  |  |  | x | Influent Influent feed pump (46 2 AP IFP 95 001) Alarm | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_46_AP_ifp_95_001.feedbackFailure.IThis.AlarmStatus
Influent.Equipment.InfluentPump.Capacity | Float |  |  |  |  | x | Influent Influent feed pump (46 2 AP IFP 95 001) Capacity
Influent.Equipment.InfluentPump.Frequency | Float |  |  |  |  | x | Influent Influent feed pump (46 2 AP IFP 95 001) Frequency
Influent.Equipment.InfluentPump.Mode | Boolean |  |  |  |  | x | Influent Influent feed pump (46 2 AP IFP 95 001) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_46_AP_ifp_95_001.IThis.Mode
Influent.Equipment.InfluentPump.Power | Float |  |  |  |  | x | Influent Influent feed pump (46 2 AP IFP 95 001) Power (kW)
Influent.Equipment.InfluentPump.Run | Boolean |  |  |  |  | x | Influent Influent feed pump (46 2 AP IFP 95 001) Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_46_AP_ifp_95_001.IThis.CurrentOp
Influent.Signal.Flow | Float |  |  |  |  | x | Influent Influent flow (46 2 VB FT 95 001) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.Sensor._46_2_VB_FT_95_001.IThis.Pv
Influent.Signal.Flow.Alarm | Boolean |  |  |  |  | x | Influent Influent flow Alarm (46 2 VB FT 95 001) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.Sensor._46_2_VB_FT_95_001.signalConditioning.ChFailureAlarm.IThis.AlarmStatus
Line01.Nereda01.Command.Reset | Boolean |  |  |  |  | x | Line01.Nereda01 reset command from SCADA | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Mode.Command.ResetReactor1
Line01.Nereda01.Equipment.AerationValve01.Alarm | Boolean |  |  |  |  | x | Line01.Nereda01 Aeration valve air grid, Alarm status (MOD NVPP 001 a-- 036) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_036.Valve.feedbackFailure.IThis.AlarmStatus
Line01.Nereda01.Equipment.AerationValve01.Closed | Boolean |  |  |  |  | x | Line01.Nereda01 Aeration valve air grid, Closed status (MOD NVPP 001 a-- 036) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_036.IThis.FbClosed
Line01.Nereda01.Equipment.AerationValve01.Mode | Boolean |  |  |  |  | x | Line01.Nereda01 Aeration valve air grid (MOD NVPP 001 a-- 036) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_036.Valve.IThis.Mode
Line01.Nereda01.Equipment.AerationValve01.Open | Boolean |  |  |  |  | x | Line01.Nereda01 Aeration valve air grid, Open status (MOD NVPP 001 a-- 036) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_036.IThis.FbOpen
Line01.Nereda01.Equipment.AerationValve02.Alarm | Boolean |  |  |  |  | x | Line01.Nereda01 Aeration valve influent grid, Alarm status (MOD NVPP 001 a-- 067) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_067.Valve.feedbackFailure.IThis.AlarmStatus
Line01.Nereda01.Equipment.AerationValve02.Closed | Boolean |  |  |  |  | x | Line01.Nereda01 Aeration valve influent grid, Closed status (MOD NVPP 001 a-- 067) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_067.IThis.FbClosed
Line01.Nereda01.Equipment.AerationValve02.Mode | Boolean |  |  |  |  | x | Line01.Nereda01 Aeration valve influent grid (MOD NVPP 001 a-- 067) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_067.Valve.IThis.Mode
Line01.Nereda01.Equipment.AerationValve02.Open | Boolean |  |  |  |  | x | Line01.Nereda01 Aeration valve influent grid, Open status (MOD NVPP 001 a-- 067) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_067.IThis.FbOpen
Line01.Nereda01.Equipment.FeedValve.Alarm | Boolean |  |  |  |  | x | Line01.Nereda01 Reactor feed valve, Alarm status (MOD NVPP 001 a-- 007) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_007.Valve.feedbackFailure.IThis.AlarmStatus
Line01.Nereda01.Equipment.FeedValve.Closed | Boolean |  |  |  |  | x | Line01.Nereda01 Reactor feed valve, Closed status (MOD NVPP 001 a-- 007) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_007.IThis.FbClosed
Line01.Nereda01.Equipment.FeedValve.Mode | Boolean |  |  |  |  | x | Line01.Nereda01 Reactor feed valve (MOD NVPP 001 a-- 007) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_007.Valve.IThis.Mode
Line01.Nereda01.Equipment.FeedValve.Open | Boolean |  |  |  |  | x | Line01.Nereda01 Reactor feed valve, Open status (MOD NVPP 001 a-- 007) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_007.IThis.FbOpen
Line01.Nereda01.Equipment.PressureReliefValve.Alarm | Boolean |  |  |  |  | x | Line01.Nereda01 Pressure relief valve, Alarm status (MOD NVPP 001 a-- 038) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_038.Valve.feedbackFailure.IThis.AlarmStatus
Line01.Nereda01.Equipment.PressureReliefValve.Closed | Boolean |  |  |  |  | x | Line01.Nereda01 Pressure relief valve, Closed status (MOD NVPP 001 a-- 038) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_038.IThis.FbClosed
Line01.Nereda01.Equipment.PressureReliefValve.Mode | Boolean |  |  |  |  | x | Line01.Nereda01 Pressure relief valve (MOD NVPP 001 a-- 038) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_038.Valve.IThis.Mode
Line01.Nereda01.Equipment.PressureReliefValve.Open | Boolean |  |  |  |  | x | Line01.Nereda01 Pressure relief valve, Open status (MOD NVPP 001 a-- 038) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_038.IThis.FbOpen
Line01.Nereda01.Equipment.SludgeDischargeValve.Alarm | Boolean |  |  |  |  | x | Line01.Nereda01 Sludge discharge valve, Alarm status (MOD NVPP 001 a-- 023) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_023.Valve.feedbackFailure.IThis.AlarmStatus
Line01.Nereda01.Equipment.SludgeDischargeValve.Closed | Boolean |  |  |  |  | x | Line01.Nereda01 Sludge discharge valve, Closed status (MOD NVPP 001 a-- 023) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_023.IThis.FbClosed
Line01.Nereda01.Equipment.SludgeDischargeValve.Mode | Boolean |  |  |  |  | x | Line01.Nereda01 Sludge discharge valve (MOD NVPP 001 a-- 023) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_023.Valve.IThis.Mode
Line01.Nereda01.Equipment.SludgeDischargeValve.Open | Boolean |  |  |  |  | x | Line01.Nereda01 Sludge discharge valve, Open status (MOD NVPP 001 a-- 023) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Actuators.VALVE_NVPP_001_a_023.IThis.FbOpen
Line01.Nereda01.Phase.Aerate.OperatingConditionsFailed | Integer |  |  |  |  | x | Line01.Nereda01 Phase Aerate Operating Conditions Failed | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.OCAerate.IThis.OC_statusword
Line01.Nereda01.Phase.Aerate.Status.Aborted | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Aerate Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Aerate.Command.ABORTED
Line01.Nereda01.Phase.Aerate.Status.Aborting | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Aerate Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Aerate.Command.ABORTING
Line01.Nereda01.Phase.Aerate.Status.Interlocked | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Aerate Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Aerate.Command.INTERLOCKED
Line01.Nereda01.Phase.Aerate.Status.Ready | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Aerate Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Aerate.Command.READY
Line01.Nereda01.Phase.Aerate.Status.Run | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Aerate Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Aerate.Command.RUN
Line01.Nereda01.Phase.Aerate.Status.Starting | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Aerate Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Aerate.Command.STARTING
Line01.Nereda01.Phase.Aerate.Status.Stopping | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Aerate Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Aerate.Command.STOPPING
Line01.Nereda01.Phase.Discharge.OperatingConditionsFailed | Integer |  |  |  |  | x | Line01.Nereda01 Phase Discharge Operating Conditions Failed | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.OCSludgeDischarge.IThis.OC_statusword
Line01.Nereda01.Phase.Discharge.Status.Aborted | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Discharge Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.SludgeDischarge.Command.ABORTED
Line01.Nereda01.Phase.Discharge.Status.Aborting | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Discharge Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.SludgeDischarge.Command.ABORTING
Line01.Nereda01.Phase.Discharge.Status.Interlocked | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Discharge Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.SludgeDischarge.Command.INTERLOCKED
Line01.Nereda01.Phase.Discharge.Status.Ready | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Discharge Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.SludgeDischarge.Command.READY
Line01.Nereda01.Phase.Discharge.Status.Run | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Discharge Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.SludgeDischarge.Command.RUN
Line01.Nereda01.Phase.Discharge.Status.Starting | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Discharge Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.SludgeDischarge.Command.STARTING
Line01.Nereda01.Phase.Discharge.Status.Stopping | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Discharge Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.SludgeDischarge.Command.STOPPING
Line01.Nereda01.Phase.Feed.OperatingConditionsFailed | Integer |  |  |  |  | x | Line01.Nereda01 Phase Feed Operating Conditions Failed | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.OCFeed.IThis.OC_Statusword
Line01.Nereda01.Phase.Feed.Status.Aborted | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Feed Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Feed.Command.ABORTED
Line01.Nereda01.Phase.Feed.Status.Aborting | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Feed Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Feed.Command.ABORTING
Line01.Nereda01.Phase.Feed.Status.Interlocked | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Feed Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Feed.Command.INTERLOCKED
Line01.Nereda01.Phase.Feed.Status.Ready | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Feed Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Feed.Command.READY
Line01.Nereda01.Phase.Feed.Status.Run | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Feed Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Feed.Command.RUN
Line01.Nereda01.Phase.Feed.Status.Starting | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Feed Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Feed.Command.STARTING
Line01.Nereda01.Phase.Feed.Status.Stopping | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Feed Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Feed.Command.STOPPING
Line01.Nereda01.Phase.Vent.OperatingConditionsFailed | Integer |  |  |  |  | x | Line01.Nereda01 Phase Vent Operating Conditions Failed | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.OCPhaseVent.IThis.OC_statusword
Line01.Nereda01.Phase.Vent.Status.Aborted | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Vent Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Vent.Command.ABORTED
Line01.Nereda01.Phase.Vent.Status.Aborting | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Vent Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Vent.Command.ABORTING
Line01.Nereda01.Phase.Vent.Status.Interlocked | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Vent Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Vent.Command.INTERLOCKED
Line01.Nereda01.Phase.Vent.Status.Ready | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Vent Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Vent.Command.READY
Line01.Nereda01.Phase.Vent.Status.Run | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Vent Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Vent.Command.RUN
Line01.Nereda01.Phase.Vent.Status.Starting | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Vent Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Vent.Command.STARTING
Line01.Nereda01.Phase.Vent.Status.Stopping | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Vent Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Vent.Command.STOPPING
Line01.Nereda01.Phase.Wait.Status.Aborted | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Wait Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Wait.Command.ABORTED
Line01.Nereda01.Phase.Wait.Status.Aborting | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Wait Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Wait.Command.ABORTING
Line01.Nereda01.Phase.Wait.Status.Interlocked | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Wait Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Wait.Command.INTERLOCKED
Line01.Nereda01.Phase.Wait.Status.Ready | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Wait Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Wait.Command.READY
Line01.Nereda01.Phase.Wait.Status.Run | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Wait Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Wait.Command.RUN
Line01.Nereda01.Phase.Wait.Status.Starting | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Wait Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Wait.Command.STARTING
Line01.Nereda01.Phase.Wait.Status.Stopping | Boolean |  |  |  |  | x | Line01.Nereda01 Phase Wait Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Wait.Command.STOPPING
Line01.Nereda01.Signal.Level | Float |  |  |  |  | x | Line01.Nereda01 Level measurement (MOD NVPP 001 LT 004) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Sensors.NVPP_001_lt_004.IThis.Pv
Line01.Nereda01.Signal.Level.Alarm | Boolean |  |  |  |  | x | Line01.Nereda01 Level measurement Alarm (MOD NVPP 001 LT 004) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Sensors.NVPP_001_lt_004.signalConditioning.ChFailureAlarm.IThis.AlarmStatus
Line01.Nereda01.Signal.O2 | Float |  |  |  |  | x | Line01.Nereda01 Disolved oxygen measurement (MOD NVPP 001 41QT1003) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Sensors.NVPP_001_41QT1003.IThis.Pv
Line01.Nereda01.Signal.O2.CommonError | Boolean |  |  |  |  | x | Line01.Nereda01 Disolved oxygen measurement CommonError bit from 16-bit analyzer status word, Bit 3 (MOD NVPP 001 41QT1003) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Sensors.NVPP_001_41QT1003.signalConditioning.ChFailureAlarm.IThis.AlarmStatus
Line01.Nereda01.Signal.pH | Float |  |  |  |  | x | Line01.Nereda01 pH measurement (MOD NVPP 001 41QT1010) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Sensors.NVPP_001_41QT1010.IThis.Pv
Line01.Nereda01.Signal.pH.CommonError | Boolean |  |  |  |  | x | Line01.Nereda01 pH measurement CommonError bit from 16-bit analyzer status word, Bit 3 (MOD NVPP 001 41QT1010) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Sensors.NVPP_001_41QT1010_Status.IThis.CommonError
Line01.Nereda01.Signal.pH.DaysToMaintenance | Integer |  |  |  |  | x | Line01.Nereda01 pH measurement DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (MOD NVPP 001 41QT1010) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Sensors.NVPP_001_41QT1010_Status.IThis.DaysToMaintenance
Line01.Nereda01.Signal.pH.Reliability | Float |  |  |  |  | x | Line01.Nereda01 pH measurement Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (MOD NVPP 001 41QT1010) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Sensors.NVPP_001_41QT1010_Status.IThis.Reliability
Line01.Nereda01.Signal.Temperature | Float |  |  |  |  | x | Line01.Nereda01 Temperature measurement (MOD NVPP 001 41QT1002) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Sensors.NVPP_001_41QT1002.IThis.Pv
Line01.Nereda01.Signal.Temperature.CommonError | Boolean |  |  |  |  | x | Line01.Nereda01 Temperature measurement CommonError bit from 16-bit analyzer status word, Bit 3 (MOD NVPP 001 41QT1002) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Sensors.NVPP_001_41QT1002_Status.IThis.CommonError
Line01.Nereda02.Command.Reset | Boolean |  |  |  |  | x | Line01.Nereda02 reset command from SCADA | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Mode.Command.ResetReactor2
Line01.Nereda02.Equipment.AerationValve01.Alarm | Boolean |  |  |  |  | x | Line01.Nereda02 Aeration valve air grid, Alarm status (MOD NVPP 001 a-- 041) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_036.Valve.feedbackFailure.IThis.AlarmStatus
Line01.Nereda02.Equipment.AerationValve01.Closed | Boolean |  |  |  |  | x | Line01.Nereda02 Aeration valve air grid, Closed status (MOD NVPP 001 a-- 041) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_036.IThis.FbClosed
Line01.Nereda02.Equipment.AerationValve01.Mode | Boolean |  |  |  |  | x | Line01.Nereda02 Aeration valve air grid (MOD NVPP 001 a-- 041) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_036.Valve.IThis.Mode
Line01.Nereda02.Equipment.AerationValve01.Open | Boolean |  |  |  |  | x | Line01.Nereda02 Aeration valve air grid, Open status (MOD NVPP 001 a-- 041) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_036.IThis.FbOpen
Line01.Nereda02.Equipment.AerationValve02.Alarm | Boolean |  |  |  |  | x | Line01.Nereda02 Aeration valve influent grid, Alarm status (MOD NVPP 001 a-- 069) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_067.Valve.feedbackFailure.IThis.AlarmStatus
Line01.Nereda02.Equipment.AerationValve02.Closed | Boolean |  |  |  |  | x | Line01.Nereda02 Aeration valve influent grid, Closed status (MOD NVPP 001 a-- 069) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_067.IThis.FbClosed
Line01.Nereda02.Equipment.AerationValve02.Mode | Boolean |  |  |  |  | x | Line01.Nereda02 Aeration valve influent grid (MOD NVPP 001 a-- 069) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_067.Valve.IThis.Mode
Line01.Nereda02.Equipment.AerationValve02.Open | Boolean |  |  |  |  | x | Line01.Nereda02 Aeration valve influent grid, Open status (MOD NVPP 001 a-- 069) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_067.IThis.FbOpen
Line01.Nereda02.Equipment.FeedValve.Alarm | Boolean |  |  |  |  | x | Line01.Nereda02 Reactor feed valve, Alarm status (MOD NVPP 001 a-- 008) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_007.Valve.feedbackFailure.IThis.AlarmStatus
Line01.Nereda02.Equipment.FeedValve.Closed | Boolean |  |  |  |  | x | Line01.Nereda02 Reactor feed valve, Closed status (MOD NVPP 001 a-- 008) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_007.IThis.FbClosed
Line01.Nereda02.Equipment.FeedValve.Mode | Boolean |  |  |  |  | x | Line01.Nereda02 Reactor feed valve (MOD NVPP 001 a-- 008) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_007.Valve.IThis.Mode
Line01.Nereda02.Equipment.FeedValve.Open | Boolean |  |  |  |  | x | Line01.Nereda02 Reactor feed valve, Open status (MOD NVPP 001 a-- 008) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_007.IThis.FbOpen
Line01.Nereda02.Equipment.PressureReliefValve.Alarm | Boolean |  |  |  |  | x | Line01.Nereda02 Pressure relief valve, Alarm status (MOD NVPP 001 a-- 043) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_038.Valve.feedbackFailure.IThis.AlarmStatus
Line01.Nereda02.Equipment.PressureReliefValve.Closed | Boolean |  |  |  |  | x | Line01.Nereda02 Pressure relief valve, Closed status (MOD NVPP 001 a-- 043) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_038.IThis.FbClosed
Line01.Nereda02.Equipment.PressureReliefValve.Mode | Boolean |  |  |  |  | x | Line01.Nereda02 Pressure relief valve (MOD NVPP 001 a-- 043) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_038.Valve.IThis.Mode
Line01.Nereda02.Equipment.PressureReliefValve.Open | Boolean |  |  |  |  | x | Line01.Nereda02 Pressure relief valve, Open status (MOD NVPP 001 a-- 043) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_038.IThis.FbOpen
Line01.Nereda02.Equipment.SludgeDischargeValve.Alarm | Boolean |  |  |  |  | x | Line01.Nereda02 Sludge discharge valve, Alarm status (MOD NVPP 001 a-- 025) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_023.Valve.feedbackFailure.IThis.AlarmStatus
Line01.Nereda02.Equipment.SludgeDischargeValve.Closed | Boolean |  |  |  |  | x | Line01.Nereda02 Sludge discharge valve, Closed status (MOD NVPP 001 a-- 025) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_023.IThis.FbClosed
Line01.Nereda02.Equipment.SludgeDischargeValve.Mode | Boolean |  |  |  |  | x | Line01.Nereda02 Sludge discharge valve (MOD NVPP 001 a-- 025) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_023.Valve.IThis.Mode
Line01.Nereda02.Equipment.SludgeDischargeValve.Open | Boolean |  |  |  |  | x | Line01.Nereda02 Sludge discharge valve, Open status (MOD NVPP 001 a-- 025) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Actuators.VALVE_NVPP_001_a_023.IThis.FbOpen
Line01.Nereda02.Phase.Aerate.OperatingConditionsFailed | Integer |  |  |  |  | x | Line01.Nereda02 Phase Aerate Operating Conditions Failed | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.OCAerate.IThis.OC_statusword
Line01.Nereda02.Phase.Aerate.Status.Aborted | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Aerate Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Aerate.Command.ABORTED
Line01.Nereda02.Phase.Aerate.Status.Aborting | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Aerate Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Aerate.Command.ABORTING
Line01.Nereda02.Phase.Aerate.Status.Interlocked | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Aerate Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Aerate.Command.INTERLOCKED
Line01.Nereda02.Phase.Aerate.Status.Ready | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Aerate Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Aerate.Command.READY
Line01.Nereda02.Phase.Aerate.Status.Run | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Aerate Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Aerate.Command.RUN
Line01.Nereda02.Phase.Aerate.Status.Starting | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Aerate Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Aerate.Command.STARTING
Line01.Nereda02.Phase.Aerate.Status.Stopping | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Aerate Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Aerate.Command.STOPPING
Line01.Nereda02.Phase.Discharge.OperatingConditionsFailed | Integer |  |  |  |  | x | Line01.Nereda02 Phase Discharge Operating Conditions Failed | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.OCSludgeDischarge.IThis.OC_statusword
Line01.Nereda02.Phase.Discharge.Status.Aborted | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Discharge Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.SludgeDischarge.Command.ABORTED
Line01.Nereda02.Phase.Discharge.Status.Aborting | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Discharge Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.SludgeDischarge.Command.ABORTING
Line01.Nereda02.Phase.Discharge.Status.Interlocked | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Discharge Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.SludgeDischarge.Command.INTERLOCKED
Line01.Nereda02.Phase.Discharge.Status.Ready | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Discharge Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.SludgeDischarge.Command.READY
Line01.Nereda02.Phase.Discharge.Status.Run | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Discharge Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.SludgeDischarge.Command.RUN
Line01.Nereda02.Phase.Discharge.Status.Starting | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Discharge Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.SludgeDischarge.Command.STARTING
Line01.Nereda02.Phase.Discharge.Status.Stopping | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Discharge Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.SludgeDischarge.Command.STOPPING
Line01.Nereda02.Phase.Feed.OperatingConditionsFailed | Integer |  |  |  |  | x | Line01.Nereda02 Phase Feed Operating Conditions Failed | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.OCFeed.IThis.OC_Statusword
Line01.Nereda02.Phase.Feed.Status.Aborted | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Feed Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Feed.Command.ABORTED
Line01.Nereda02.Phase.Feed.Status.Aborting | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Feed Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Feed.Command.ABORTING
Line01.Nereda02.Phase.Feed.Status.Interlocked | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Feed Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Feed.Command.INTERLOCKED
Line01.Nereda02.Phase.Feed.Status.Ready | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Feed Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Feed.Command.READY
Line01.Nereda02.Phase.Feed.Status.Run | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Feed Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Feed.Command.RUN
Line01.Nereda02.Phase.Feed.Status.Starting | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Feed Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Feed.Command.STARTING
Line01.Nereda02.Phase.Feed.Status.Stopping | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Feed Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Feed.Command.STOPPING
Line01.Nereda02.Phase.Vent.OperatingConditionsFailed | Integer |  |  |  |  | x | Line01.Nereda02 Phase Vent Operating Conditions Failed | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.OCPhaseVent.IThis.OC_statusword
Line01.Nereda02.Phase.Vent.Status.Aborted | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Vent Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Vent.Command.ABORTED
Line01.Nereda02.Phase.Vent.Status.Aborting | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Vent Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Vent.Command.ABORTING
Line01.Nereda02.Phase.Vent.Status.Interlocked | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Vent Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Vent.Command.INTERLOCKED
Line01.Nereda02.Phase.Vent.Status.Ready | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Vent Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Vent.Command.READY
Line01.Nereda02.Phase.Vent.Status.Run | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Vent Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Vent.Command.RUN
Line01.Nereda02.Phase.Vent.Status.Starting | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Vent Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Vent.Command.STARTING
Line01.Nereda02.Phase.Vent.Status.Stopping | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Vent Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Vent.Command.STOPPING
Line01.Nereda02.Phase.Wait.Status.Aborted | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Wait Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Wait.Command.ABORTED
Line01.Nereda02.Phase.Wait.Status.Aborting | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Wait Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Wait.Command.ABORTING
Line01.Nereda02.Phase.Wait.Status.Interlocked | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Wait Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Wait.Command.INTERLOCKED
Line01.Nereda02.Phase.Wait.Status.Ready | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Wait Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Wait.Command.READY
Line01.Nereda02.Phase.Wait.Status.Run | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Wait Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Wait.Command.RUN
Line01.Nereda02.Phase.Wait.Status.Starting | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Wait Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Wait.Command.STARTING
Line01.Nereda02.Phase.Wait.Status.Stopping | Boolean |  |  |  |  | x | Line01.Nereda02 Phase Wait Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Wait.Command.STOPPING
Line01.Nereda02.Signal.Level | Float |  |  |  |  | x | Line01.Nereda02 Level measurement (MOD NVPP 001 LT 005) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Sensors.NVPP_001_lt_004.IThis.Pv
Line01.Nereda02.Signal.Level.Alarm | Boolean |  |  |  |  | x | Line01.Nereda02 Level measurement Alarm (MOD NVPP 001 LT 005) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Sensors.NVPP_001_lt_004.signalConditioning.ChFailureAlarm.IThis.AlarmStatus
Line01.Nereda02.Signal.O2 | Float |  |  |  |  | x | Line01.Nereda02 Disolved oxygen measurement (MOD NVPP 001 42QT1003) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Sensors.NVPP_001_41QT1003.IThis.Pv
Line01.Nereda02.Signal.O2.CommonError | Boolean |  |  |  |  | x | Line01.Nereda02 Disolved oxygen measurement CommonError bit from 16-bit analyzer status word, Bit 3 (MOD NVPP 001 42QT1003)
Line01.Nereda02.Signal.pH | Float |  |  |  |  | x | Line01.Nereda02 pH measurement (MOD NVPP 001 42QT1010) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Sensors.NVPP_001_41QT1010.IThis.Pv
Line01.Nereda02.Signal.pH.CommonError | Boolean |  |  |  |  | x | Line01.Nereda02 pH measurement CommonError bit from 16-bit analyzer status word, Bit 3 (MOD NVPP 001 42QT1010) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Sensors.NVPP_001_41QT1010_Status.IThis.CommonError
Line01.Nereda02.Signal.pH.DaysToMaintenance | Integer |  |  |  |  | x | Line01.Nereda02 pH measurement DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (MOD NVPP 001 42QT1010) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Sensors.NVPP_001_41QT1010_Status.IThis.DaysToMaintenance
Line01.Nereda02.Signal.pH.Reliability | Float |  |  |  |  | x | Line01.Nereda02 pH measurement Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (MOD NVPP 001 42QT1010) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Sensors.NVPP_001_41QT1010_Status.IThis.Reliability
Line01.Nereda02.Signal.Temperature | Float |  |  |  |  | x | Line01.Nereda02 Temperature measurement (MOD NVPP 001 42QT1002) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Sensors.NVPP_001_41QT1002.IThis.Pv
Line01.Nereda02.Signal.Temperature.CommonError | Boolean |  |  |  |  | x | Line01.Nereda02 Temperature measurement CommonError bit from 16-bit analyzer status word, Bit 3 (MOD NVPP 001 42QT1002) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Sensors.NVPP_001_41QT1002_Status.IThis.CommonError
Line01.Nereda03.Command.Reset | Boolean |  |  |  |  | x | Line01.Nereda03 reset command from SCADA | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Mode.Command.ResetReactor3
Line01.Nereda03.Equipment.AerationValve01.Alarm | Boolean |  |  |  |  | x | Line01.Nereda03 Aeration valve air grid, Alarm status (MOD NVPP 001 a-- 046) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_036.Valve.feedbackFailure.IThis.AlarmStatus
Line01.Nereda03.Equipment.AerationValve01.Closed | Boolean |  |  |  |  | x | Line01.Nereda03 Aeration valve air grid, Closed status (MOD NVPP 001 a-- 046) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_036.IThis.FbClosed
Line01.Nereda03.Equipment.AerationValve01.Mode | Boolean |  |  |  |  | x | Line01.Nereda03 Aeration valve air grid (MOD NVPP 001 a-- 046) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_036.Valve.IThis.Mode
Line01.Nereda03.Equipment.AerationValve01.Open | Boolean |  |  |  |  | x | Line01.Nereda03 Aeration valve air grid, Open status (MOD NVPP 001 a-- 046) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_036.IThis.FbOpen
Line01.Nereda03.Equipment.AerationValve02.Alarm | Boolean |  |  |  |  | x | Line01.Nereda03 Aeration valve influent grid, Alarm status (MOD NVPP 001 a-- 071) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_067.Valve.feedbackFailure.IThis.AlarmStatus
Line01.Nereda03.Equipment.AerationValve02.Closed | Boolean |  |  |  |  | x | Line01.Nereda03 Aeration valve influent grid, Closed status (MOD NVPP 001 a-- 071) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_067.IThis.FbClosed
Line01.Nereda03.Equipment.AerationValve02.Mode | Boolean |  |  |  |  | x | Line01.Nereda03 Aeration valve influent grid (MOD NVPP 001 a-- 071) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_067.Valve.IThis.Mode
Line01.Nereda03.Equipment.AerationValve02.Open | Boolean |  |  |  |  | x | Line01.Nereda03 Aeration valve influent grid, Open status (MOD NVPP 001 a-- 071) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_067.IThis.FbOpen
Line01.Nereda03.Equipment.FeedValve.Alarm | Boolean |  |  |  |  | x | Line01.Nereda03 Reactor feed valve, Alarm status (MOD NVPP 001 a-- 009) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_007.Valve.feedbackFailure.IThis.AlarmStatus
Line01.Nereda03.Equipment.FeedValve.Closed | Boolean |  |  |  |  | x | Line01.Nereda03 Reactor feed valve, Closed status (MOD NVPP 001 a-- 009) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_007.IThis.FbClosed
Line01.Nereda03.Equipment.FeedValve.Mode | Boolean |  |  |  |  | x | Line01.Nereda03 Reactor feed valve (MOD NVPP 001 a-- 009) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_007.Valve.IThis.Mode
Line01.Nereda03.Equipment.FeedValve.Open | Boolean |  |  |  |  | x | Line01.Nereda03 Reactor feed valve, Open status (MOD NVPP 001 a-- 009) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_007.IThis.FbOpen
Line01.Nereda03.Equipment.PressureReliefValve.Alarm | Boolean |  |  |  |  | x | Line01.Nereda03 Pressure relief valve, Alarm status (MOD NVPP 001 a-- 048) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_038.Valve.feedbackFailure.IThis.AlarmStatus
Line01.Nereda03.Equipment.PressureReliefValve.Closed | Boolean |  |  |  |  | x | Line01.Nereda03 Pressure relief valve, Closed status (MOD NVPP 001 a-- 048) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_038.IThis.FbClosed
Line01.Nereda03.Equipment.PressureReliefValve.Mode | Boolean |  |  |  |  | x | Line01.Nereda03 Pressure relief valve (MOD NVPP 001 a-- 048) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_038.Valve.IThis.Mode
Line01.Nereda03.Equipment.PressureReliefValve.Open | Boolean |  |  |  |  | x | Line01.Nereda03 Pressure relief valve, Open status (MOD NVPP 001 a-- 048) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_038.IThis.FbOpen
Line01.Nereda03.Equipment.SludgeDischargeValve.Alarm | Boolean |  |  |  |  | x | Line01.Nereda03 Sludge discharge valve, Alarm status (MOD NVPP 001 a-- 027) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_023.Valve.feedbackFailure.IThis.AlarmStatus
Line01.Nereda03.Equipment.SludgeDischargeValve.Closed | Boolean |  |  |  |  | x | Line01.Nereda03 Sludge discharge valve, Closed status (MOD NVPP 001 a-- 027) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_023.IThis.FbClosed
Line01.Nereda03.Equipment.SludgeDischargeValve.Mode | Boolean |  |  |  |  | x | Line01.Nereda03 Sludge discharge valve (MOD NVPP 001 a-- 027) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_023.Valve.IThis.Mode
Line01.Nereda03.Equipment.SludgeDischargeValve.Open | Boolean |  |  |  |  | x | Line01.Nereda03 Sludge discharge valve, Open status (MOD NVPP 001 a-- 027) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Actuators.VALVE_NVPP_001_a_023.IThis.FbOpen
Line01.Nereda03.Phase.Aerate.OperatingConditionsFailed | Integer |  |  |  |  | x | Line01.Nereda03 Phase Aerate Operating Conditions Failed | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.OCAerate.IThis.OC_statusword
Line01.Nereda03.Phase.Aerate.Status.Aborted | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Aerate Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Aerate.Command.ABORTED
Line01.Nereda03.Phase.Aerate.Status.Aborting | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Aerate Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Aerate.Command.ABORTING
Line01.Nereda03.Phase.Aerate.Status.Interlocked | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Aerate Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Aerate.Command.INTERLOCKED
Line01.Nereda03.Phase.Aerate.Status.Ready | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Aerate Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Aerate.Command.READY
Line01.Nereda03.Phase.Aerate.Status.Run | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Aerate Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Aerate.Command.RUN
Line01.Nereda03.Phase.Aerate.Status.Starting | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Aerate Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Aerate.Command.STARTING
Line01.Nereda03.Phase.Aerate.Status.Stopping | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Aerate Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Aerate.Command.STOPPING
Line01.Nereda03.Phase.Discharge.OperatingConditionsFailed | Integer |  |  |  |  | x | Line01.Nereda03 Phase Discharge Operating Conditions Failed | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.OCSludgeDischarge.IThis.OC_statusword
Line01.Nereda03.Phase.Discharge.Status.Aborted | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Discharge Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.SludgeDischarge.Command.ABORTED
Line01.Nereda03.Phase.Discharge.Status.Aborting | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Discharge Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.SludgeDischarge.Command.ABORTING
Line01.Nereda03.Phase.Discharge.Status.Interlocked | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Discharge Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.SludgeDischarge.Command.INTERLOCKED
Line01.Nereda03.Phase.Discharge.Status.Ready | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Discharge Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.SludgeDischarge.Command.READY
Line01.Nereda03.Phase.Discharge.Status.Run | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Discharge Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.SludgeDischarge.Command.RUN
Line01.Nereda03.Phase.Discharge.Status.Starting | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Discharge Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.SludgeDischarge.Command.STARTING
Line01.Nereda03.Phase.Discharge.Status.Stopping | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Discharge Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.SludgeDischarge.Command.STOPPING
Line01.Nereda03.Phase.Feed.OperatingConditionsFailed | Integer |  |  |  |  | x | Line01.Nereda03 Phase Feed Operating Conditions Failed | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.OCFeed.IThis.OC_Statusword
Line01.Nereda03.Phase.Feed.Status.Aborted | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Feed Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Feed.Command.ABORTED
Line01.Nereda03.Phase.Feed.Status.Aborting | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Feed Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Feed.Command.ABORTING
Line01.Nereda03.Phase.Feed.Status.Interlocked | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Feed Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Feed.Command.INTERLOCKED
Line01.Nereda03.Phase.Feed.Status.Ready | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Feed Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Feed.Command.READY
Line01.Nereda03.Phase.Feed.Status.Run | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Feed Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Feed.Command.RUN
Line01.Nereda03.Phase.Feed.Status.Starting | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Feed Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Feed.Command.STARTING
Line01.Nereda03.Phase.Feed.Status.Stopping | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Feed Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Feed.Command.STOPPING
Line01.Nereda03.Phase.Vent.OperatingConditionsFailed | Integer |  |  |  |  | x | Line01.Nereda03 Phase Vent Operating Conditions Failed | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.OCPhaseVent.IThis.OC_statusword
Line01.Nereda03.Phase.Vent.Status.Aborted | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Vent Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Vent.Command.ABORTED
Line01.Nereda03.Phase.Vent.Status.Aborting | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Vent Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Vent.Command.ABORTING
Line01.Nereda03.Phase.Vent.Status.Interlocked | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Vent Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Vent.Command.INTERLOCKED
Line01.Nereda03.Phase.Vent.Status.Ready | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Vent Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Vent.Command.READY
Line01.Nereda03.Phase.Vent.Status.Run | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Vent Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Vent.Command.RUN
Line01.Nereda03.Phase.Vent.Status.Starting | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Vent Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Vent.Command.STARTING
Line01.Nereda03.Phase.Vent.Status.Stopping | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Vent Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Vent.Command.STOPPING
Line01.Nereda03.Phase.Wait.Status.Aborted | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Wait Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Wait.Command.ABORTED
Line01.Nereda03.Phase.Wait.Status.Aborting | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Wait Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Wait.Command.ABORTING
Line01.Nereda03.Phase.Wait.Status.Interlocked | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Wait Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Wait.Command.INTERLOCKED
Line01.Nereda03.Phase.Wait.Status.Ready | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Wait Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Wait.Command.READY
Line01.Nereda03.Phase.Wait.Status.Run | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Wait Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Wait.Command.RUN
Line01.Nereda03.Phase.Wait.Status.Starting | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Wait Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Wait.Command.STARTING
Line01.Nereda03.Phase.Wait.Status.Stopping | Boolean |  |  |  |  | x | Line01.Nereda03 Phase Wait Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Wait.Command.STOPPING
Line01.Nereda03.Signal.Level | Float |  |  |  |  | x | Line01.Nereda03 Level measurement (MOD NVPP 001 LT 006) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Sensors.NVPP_001_lt_004.IThis.Pv
Line01.Nereda03.Signal.Level.Alarm | Boolean |  |  |  |  | x | Line01.Nereda03 Level measurement Alarm (MOD NVPP 001 LT 006) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Sensors.NVPP_001_lt_004.signalConditioning.ChFailureAlarm.IThis.AlarmStatus
Line01.Nereda03.Signal.O2 | Float |  |  |  |  | x | Line01.Nereda03 Disolved oxygen measurement (MOD NVPP 001 43QT1003) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Sensors.NVPP_001_41QT1003.IThis.Pv
Line01.Nereda03.Signal.O2.CommonError | Boolean |  |  |  |  | x | Line01.Nereda03 Disolved oxygen measurement CommonError bit from 16-bit analyzer status word, Bit 3 (MOD NVPP 001 43QT1003) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Sensors.NVPP_001_41QT1003.signalConditioning.ChFailureAlarm.IThis.AlarmStatus
Line01.Nereda03.Signal.pH | Float |  |  |  |  | x | Line01.Nereda03 pH measurement (MOD NVPP 001 43QT1010) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Sensors.NVPP_001_41QT1010.IThis.Pv
Line01.Nereda03.Signal.pH.CommonError | Boolean |  |  |  |  | x | Line01.Nereda03 pH measurement CommonError bit from 16-bit analyzer status word, Bit 3 (MOD NVPP 001 43QT1010) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Sensors.NVPP_001_41QT1010_Status.IThis.CommonError
Line01.Nereda03.Signal.pH.DaysToMaintenance | Integer |  |  |  |  | x | Line01.Nereda03 pH measurement DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (MOD NVPP 001 43QT1010) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Sensors.NVPP_001_41QT1010_Status.IThis.DaysToMaintenance
Line01.Nereda03.Signal.pH.Reliability | Float |  |  |  |  | x | Line01.Nereda03 pH measurement Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (MOD NVPP 001 43QT1010) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Sensors.NVPP_001_41QT1010_Status.IThis.Reliability
Line01.Nereda03.Signal.Temperature | Float |  |  |  |  | x | Line01.Nereda03 Temperature measurement (MOD NVPP 001 43QT1002) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Sensors.NVPP_001_41QT1002.IThis.Pv
Line01.Nereda03.Signal.Temperature.CommonError | Boolean |  |  |  |  | x | Line01.Nereda03 Temperature measurement CommonError bit from 16-bit analyzer status word, Bit 3 (MOD NVPP 001 43QT1002) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Sensors.NVPP_001_41QT1002_Status.IThis.CommonError
NeredaController.Status.Auto | Boolean | [5 empty] | Nereda Controller switched to Auto from SCADA | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Mode.Command.Auto
NeredaController.Status.EmergencyRecipe | Boolean | [5 empty] | EmergencyRecipeStatus signal; when 1, the reactors are in emergency recipe | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Mode.Command.Emergency
NeredaController.Status.Manual | Boolean | [5 empty] | Nereda Controller switched to Manual from SCADA | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Mode.Command.Manual
NeredaController.Status.Off | Boolean | [5 empty] | Nereda Controller switched to Off from SCADA | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Mode.Command.OFF
Plant.Signal.PowerNOK | Boolean | [5 empty] | Invert of Power OK signal; Scale=-1 Offset=1 | [7 empty] | SoftdPAC_BX1_NVPP.RES0.MCCPower.IThis.MCCPower
Screens.Equipment.BackwashWaterValve.Alarm | Boolean |  |  |  |  | x | Screens Screen backwash water valve, Alarm status (MOD NVPP 001 a-- 016) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_016.Valve.feedbackFailure.IThis.AlarmStatus
Screens.Equipment.BackwashWaterValve.Closed | Boolean |  |  |  |  | x | Screens Screen backwash water valve, Closed status (MOD NVPP 001 a-- 016) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_016.IThis.FbClosed
Screens.Equipment.BackwashWaterValve.Mode | Boolean |  |  |  |  | x | Screens Screen backwash water valve (MOD NVPP 001 a-- 016) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_016.Valve.IThis.Mode
Screens.Equipment.BackwashWaterValve.Open | Boolean |  |  |  |  | x | Screens Screen backwash water valve, Open status (MOD NVPP 001 a-- 016) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_016.IThis.FbOpen
Screens.Equipment.Screen.Alarm | Boolean |  |  |  |  | x | Screens Screen (MOD NVPP 001 RGI 001) Alarm | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_001_RGI_001.feedbackFailure.IThis.AlarmStatus
Screens.Equipment.Screen.Mode | Boolean |  |  |  |  | x | Screens Screen (MOD NVPP 001 RGI 001) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_001_RGI_001.IThis.Mode
Screens.Equipment.Screen.Power | Float |  |  |  |  | x | Screens Screen (MOD NVPP 001 RGI 001) Power (kW)
Screens.Equipment.Screen.Run | Boolean |  |  |  |  | x | Screens Screen (MOD NVPP 001 RGI 001) Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Influent.NVPP_001_RGI_001.IThis.CurrentOp
Screens.Equipment.SpentBackwashWaterValve.Alarm | Boolean |  |  |  |  | x | Screens Screen spent backwash water valve, Alarm status (MOD NVPP 001 a-- 002) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_002.Valve.feedbackFailure.IThis.AlarmStatus
Screens.Equipment.SpentBackwashWaterValve.Closed | Boolean |  |  |  |  | x | Screens Screen spent backwash water valve, Closed status (MOD NVPP 001 a-- 002) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_002.IThis.FbClosed
Screens.Equipment.SpentBackwashWaterValve.Mode | Boolean |  |  |  |  | x | Screens Screen spent backwash water valve (MOD NVPP 001 a-- 002) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_002.Valve.IThis.Mode
Screens.Equipment.SpentBackwashWaterValve.Open | Boolean |  |  |  |  | x | Screens Screen spent backwash water valve, Open status (MOD NVPP 001 a-- 002) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_002.IThis.FbOpen
SludgeBuffer01.Command.Reset | Boolean |  |  |  |  | x | SludgeBuffer01 reset command from SCADA | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Mode.Command.Auto_Off_Manu
SludgeBuffer01.Equipment.DrainValve.Alarm | Boolean |  |  |  |  | x | SludgeBuffer01 Sludge discharge drain valve, Alarm status (46 2 AP a-- 95 008) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_46_2_AP_a_95_008.Valve.feedbackFailure.IThis.AlarmStatus
SludgeBuffer01.Equipment.DrainValve.Closed | Boolean |  |  |  |  | x | SludgeBuffer01 Sludge discharge drain valve, Closed status (46 2 AP a-- 95 008) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_46_2_AP_a_95_008.IThis.FbClosed
SludgeBuffer01.Equipment.DrainValve.Mode | Boolean |  |  |  |  | x | SludgeBuffer01 Sludge discharge drain valve (46 2 AP a-- 95 008) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_46_2_AP_a_95_008.Valve.IThis.Mode
SludgeBuffer01.Equipment.DrainValve.Open | Boolean |  |  |  |  | x | SludgeBuffer01 Sludge discharge drain valve, Open status (46 2 AP a-- 95 008) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_46_2_AP_a_95_008.IThis.FbOpen
SludgeBuffer01.Equipment.SludgeDischargePump.Alarm | Boolean |  |  |  |  | x | SludgeBuffer01 Sludge discharge pump (MOD NVPP 001 sbp 001) Alarm | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SludgeBufferPump.NVPP_001_sbp_001.Pump.feedbackFailure.IThis.AlarmStatus
SludgeBuffer01.Equipment.SludgeDischargePump.Mode | Boolean |  |  |  |  | x | SludgeBuffer01 Sludge discharge pump (MOD NVPP 001 sbp 001) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SludgeBufferPump.NVPP_001_sbp_001.Pump.IThis.Mode
SludgeBuffer01.Equipment.SludgeDischargePump.Power | Float |  |  |  |  | x | SludgeBuffer01 Sludge discharge pump (MOD NVPP 001 sbp 001) Power (kW)
SludgeBuffer01.Equipment.SludgeDischargePump.RPM | Float |  |  |  |  | x | SludgeBuffer01 Sludge discharge pump (MOD NVPP 001 sbp 001) RPM | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SludgeBufferPump.NVPP_001_sbp_001.Pump.IThis.SpeedPv
SludgeBuffer01.Equipment.SludgeDischargePump.Run | Boolean |  |  |  |  | x | SludgeBuffer01 Sludge discharge pump (MOD NVPP 001 sbp 001) Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SludgeBufferPump.NVPP_001_sbp_001.Pump.IThis.CurrentOp
SludgeBuffer01.Equipment.SludgeDischargeValve.Alarm | Boolean |  |  |  |  | x | SludgeBuffer01 Pre-Thickened Sludge Outlet Actuated Valve (P&ID A6S/11854-XZ-90702), Alarm status (MOD NVPP 001 a-- 029) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.NVPP_001_a_029.Valve.feedbackFailure.IThis.AlarmStatus
SludgeBuffer01.Equipment.SludgeDischargeValve.Closed | Boolean |  |  |  |  | x | SludgeBuffer01 Pre-Thickened Sludge Outlet Actuated Valve (P&ID A6S/11854-XZ-90702), Closed status (MOD NVPP 001 a-- 029) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.NVPP_001_a_029.IThis.FbClosed
SludgeBuffer01.Equipment.SludgeDischargeValve.Mode | Boolean |  |  |  |  | x | SludgeBuffer01 Pre-Thickened Sludge Outlet Actuated Valve (P&ID A6S/11854-XZ-90702) (MOD NVPP 001 a-- 029) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.NVPP_001_a_029.Valve.IThis.Mode
SludgeBuffer01.Equipment.SludgeDischargeValve.Open | Boolean |  |  |  |  | x | SludgeBuffer01 Pre-Thickened Sludge Outlet Actuated Valve (P&ID A6S/11854-XZ-90702), Open status (MOD NVPP 001 a-- 029) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.NVPP_001_a_029.IThis.FbOpen
SludgeBuffer01.Equipment.WashWaterValve.Alarm | Boolean |  |  |  |  | x | SludgeBuffer01 Wash water valve, Alarm status (MOD NVPP 001 a-- 017) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_017.Valve.feedbackFailure.IThis.AlarmStatus
SludgeBuffer01.Equipment.WashWaterValve.Closed | Boolean |  |  |  |  | x | SludgeBuffer01 Wash water valve, Closed status (MOD NVPP 001 a-- 017) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_017.IThis.FbClosed
SludgeBuffer01.Equipment.WashWaterValve.Mode | Boolean |  |  |  |  | x | SludgeBuffer01 Wash water valve (MOD NVPP 001 a-- 017) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_017.Valve.IThis.Mode
SludgeBuffer01.Equipment.WashWaterValve.Open | Boolean |  |  |  |  | x | SludgeBuffer01 Wash water valve, Open status (MOD NVPP 001 a-- 017) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_001_a_017.IThis.FbOpen
SludgeBuffer01.Phase.SB_Feed.OperatingConditionsFailed | Integer |  |  |  |  | x | SludgeBuffer01 Phase Feed Operating Conditions Failed | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.OC_SB_Feed.IThis.OC_statusword
SludgeBuffer01.Phase.SB_Feed.Status.Aborted | Boolean |  |  |  |  | x | SludgeBuffer01 Phase Feed Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.Feed.Command.ABORTED
SludgeBuffer01.Phase.SB_Feed.Status.Aborting | Boolean |  |  |  |  | x | SludgeBuffer01 Phase Feed Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.Feed.Command.ABORTING
SludgeBuffer01.Phase.SB_Feed.Status.Interlocked | Boolean |  |  |  |  | x | SludgeBuffer01 Phase Feed Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.Feed.Command.INTERLOCKED
SludgeBuffer01.Phase.SB_Feed.Status.Ready | Boolean |  |  |  |  | x | SludgeBuffer01 Phase Feed Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.Feed.Command.READY
SludgeBuffer01.Phase.SB_Feed.Status.Run | Boolean |  |  |  |  | x | SludgeBuffer01 Phase Feed Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.Feed.Command.RUN
SludgeBuffer01.Phase.SB_Feed.Status.Starting | Boolean |  |  |  |  | x | SludgeBuffer01 Phase Feed Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.Feed.Command.STARTING
SludgeBuffer01.Phase.SB_Feed.Status.Stopping | Boolean |  |  |  |  | x | SludgeBuffer01 Phase Feed Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.Feed.Command.STOPPING
SludgeBuffer01.Phase.SB_SludgeDischarge.OperatingConditionsFailed | Integer |  |  |  |  | x | SludgeBuffer01 Phase SludgeDischarge Operating Conditions Failed | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.OC_SB_Discharge.IThis.OC_statusword
SludgeBuffer01.Phase.SB_SludgeDischarge.Status.Aborted | Boolean |  |  |  |  | x | SludgeBuffer01 Phase SludgeDischarge Status Aborted | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.SludgeDischarge.Command.ABORTED
SludgeBuffer01.Phase.SB_SludgeDischarge.Status.Aborting | Boolean |  |  |  |  | x | SludgeBuffer01 Phase SludgeDischarge Status Aborting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.SludgeDischarge.Command.ABORTING
SludgeBuffer01.Phase.SB_SludgeDischarge.Status.Interlocked | Boolean |  |  |  |  | x | SludgeBuffer01 Phase SludgeDischarge Status Interlocked | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.SludgeDischarge.Command.INTERLOCKED
SludgeBuffer01.Phase.SB_SludgeDischarge.Status.Ready | Boolean |  |  |  |  | x | SludgeBuffer01 Phase SludgeDischarge Status Ready | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.SludgeDischarge.Command.READY
SludgeBuffer01.Phase.SB_SludgeDischarge.Status.Run | Boolean |  |  |  |  | x | SludgeBuffer01 Phase SludgeDischarge Status Run | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.SludgeDischarge.Command.RUN
SludgeBuffer01.Phase.SB_SludgeDischarge.Status.Starting | Boolean |  |  |  |  | x | SludgeBuffer01 Phase SludgeDischarge Status Starting | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.SludgeDischarge.Command.STARTING
SludgeBuffer01.Phase.SB_SludgeDischarge.Status.Stopping | Boolean |  |  |  |  | x | SludgeBuffer01 Phase SludgeDischarge Status Stopping | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.SludgeDischarge.Command.STOPPING
SludgeBuffer01.Signal.Level | Float |  |  |  |  | x | SludgeBuffer01 Level measurement (MOD NVPP 001 LT 003) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.Sensor.NVPP_001_lt_003.IThis.Pv
SludgeBuffer01.Signal.Level.Alarm | Boolean |  |  |  |  | x | SludgeBuffer01 Level measurement Alarm (MOD NVPP 001 LT 003) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.Sensor.NVPP_001_lt_003.signalConditioning.ChFailureAlarm.IThis.AlarmStatus
Utilities.EmergencyPit.Signal.Level | Float |  |  |  |  | x | Utilities Level of emergency pit (46 2 AP LT 95 001) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_46_2_AP_LT_95_001.IThis.Pv
Utilities.EmergencyPit.Signal.Level.Alarm | Boolean |  |  |  |  | x | Utilities Level of emergency pit Alarm (46 2 AP LT 95 001) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_EffluentSensors.NVPP_46_2_AP_LT_95_001.signalConditioning.ChFailureAlarm.IThis.AlarmStatus
Utilities.Equipment.DrainValve.Alarm | Boolean |  |  |  |  | x | Utilities Emergency pit discharge drain valve, Alarm status (46 2 AP a-- 95 010) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_46_2_AP_a_95_010.Valve.feedbackFailure.IThis.AlarmStatus
Utilities.Equipment.DrainValve.Closed | Boolean |  |  |  |  | x | Utilities Emergency pit discharge drain valve, Closed status (46 2 AP a-- 95 010) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_46_2_AP_a_95_010.IThis.FbClosed
Utilities.Equipment.DrainValve.Mode | Boolean |  |  |  |  | x | Utilities Emergency pit discharge drain valve (46 2 AP a-- 95 010) Mode from SCADA (0=Manual, 1=Auto) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_46_2_AP_a_95_010.Valve.IThis.Mode
Utilities.Equipment.DrainValve.Open | Boolean |  |  |  |  | x | Utilities Emergency pit discharge drain valve, Open status (46 2 AP a-- 95 010) | [7 empty] | SoftdPAC_BX1_NVPP.RES0.NVPP_Effluent.NVPP_46_2_AP_a_95_010.IThis.FbOpen

## ToPLC
NVPP
Interfacelist with signals that Aquasuite writes to PLC
BJ2002
Version 1.1 11/06/2024
Aquasuite signals ToPLC | DataType | Scale | Bit | Address/ register | Bit rack | Description | Unit of Meas | Remarks client | Remarks RHDHV | EAE_OPCUA_TAG
FeedBuffer.Phase.FB_MetalDosing.Command.Start | Boolean |  |  |  |  | FeedBuffer Phase MetalDosing Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.MetalSaltDosinglogic.PhaseMetalSaltDosing.Command.Start_NeredaController
FeedBuffer.Phase.FB_MetalDosing.Command.Stop | Boolean |  |  |  |  | FeedBuffer Phase MetalDosing Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_MetalSaltDosing.MetalSaltDosinglogic.PhaseMetalSaltDosing.Command.Stop_NeredaController
FeedBuffer.Phase.FB_MetalDosing.Control.Capacity | Float |  |  |  |  | FeedBuffer Phase MetalDosing required metals capacity (0..100%)
HeartBeat | Boolean |  |  |  |  | Heartbeat signal from Nereda Controller to PLC |  |  |  | SoftdPAC_BX1_NVPP.RES0.HeartBeat.IThis_ForOPCUA.HeartBeat_Nereda_to_PLC
Line01.Nereda01.Phase.Aerate.Command.Start | Boolean |  |  |  |  | Line01.Nereda01 Phase Aerate Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Aerate.Command.Start_NeredaController
Line01.Nereda01.Phase.Aerate.Command.Stop | Boolean |  |  |  |  | Line01.Nereda01 Phase Aerate Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Aerate.Command.Stop_NeredaController
Line01.Nereda01.Phase.Aerate.Control.Capacity | Float |  |  |  |  | Line01.Nereda01 Required aeration capacity (0..100%) |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.LogicAerate.IThis.RunCapacity_Blower
Line01.Nereda01.Phase.Aerate.Control.AirGrid | Boolean |  |  |  |  | Line01.Nereda01 Aeration via air grid (diffusers) |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.LogicAerate.IThis.AerationGrid
Line01.Nereda01.Phase.Aerate.Control.InfluentGrid | Boolean |  |  |  |  | Line01.Nereda01 Aeration via influent grid (feed pipes) |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.LogicAerate.IThis.InfluentGrid
Line01.Nereda01.Phase.Discharge.Command.Start | Boolean |  |  |  |  | Line01.Nereda01 Phase Discharge Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.SludgeDischarge.Command.Start_NeredaController
Line01.Nereda01.Phase.Discharge.Command.Stop | Boolean |  |  |  |  | Line01.Nereda01 Phase Discharge Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.SludgeDischarge.Command.Stop_NeredaController
Line01.Nereda01.Phase.Feed.Command.Start | Boolean |  |  |  |  | Line01.Nereda01 Phase Feed Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Feed.Command.Start_NeredaController
Line01.Nereda01.Phase.Feed.Command.Stop | Boolean |  |  |  |  | Line01.Nereda01 Phase Feed Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Feed.Command.Stop_NeredaController
Line01.Nereda01.Phase.Feed.Control.FlowSetpoint | Float |  |  |  |  | Line01.Nereda01 feed flow setpoint |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.LogicFeed.IThis.Feed_Flow_SP
Line01.Nereda01.Phase.Vent.Command.Start | Boolean |  |  |  |  | Line01.Nereda01 Phase Vent Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Vent.Command.Start_NeredaController
Line01.Nereda01.Phase.Vent.Command.Stop | Boolean |  |  |  |  | Line01.Nereda01 Phase Vent Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Vent.Command.Stop_NeredaController
Line01.Nereda01.Phase.Vent.Control.AirGrid | Boolean |  |  |  |  | Line01.Nereda01 Vent air grid (diffusers) |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.LogicPhaseVent.IThis.VentAirGrid
Line01.Nereda01.Phase.Vent.Control.InfluentGrid | Boolean |  |  |  |  | Line01.Nereda01 Vent influent grid (feed pipes) |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.LogicPhaseVent.IThis.VentInfluentGrid
Line01.Nereda01.Phase.Wait.Command.Start | Boolean |  |  |  |  | Line01.Nereda01 Phase Wait Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Wait.Command.Start_NeredaController
Line01.Nereda01.Phase.Wait.Command.Stop | Boolean |  |  |  |  | Line01.Nereda01 Phase Wait Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.Reactorlogic.Wait.Command.Stop_NeredaController
Line01.Nereda01.Status | Integer |  |  |  |  | Line01.Nereda01 status for display on SCADA |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor01.IThis.Status
Line01.Nereda02.Phase.Aerate.Command.Start | Boolean |  |  |  |  | Line01.Nereda02 Phase Aerate Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Aerate.Command.Start_NeredaController
Line01.Nereda02.Phase.Aerate.Command.Stop | Boolean |  |  |  |  | Line01.Nereda02 Phase Aerate Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Aerate.Command.Stop_NeredaController
Line01.Nereda02.Phase.Aerate.Control.Capacity | Float |  |  |  |  | Line01.Nereda02 Required aeration capacity (0..100%) |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.LogicAerate.IThis.RunCapacity_Blower
Line01.Nereda02.Phase.Aerate.Control.AirGrid | Boolean |  |  |  |  | Line01.Nereda02 Aeration via air grid (diffusers) |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.LogicAerate.IThis.AerationGrid
Line01.Nereda02.Phase.Aerate.Control.InfluentGrid | Boolean |  |  |  |  | Line01.Nereda02 Aeration via influent grid (feed pipes) |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.LogicAerate.IThis.InfluentGrid
Line01.Nereda02.Phase.Discharge.Command.Start | Boolean |  |  |  |  | Line01.Nereda02 Phase Discharge Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.SludgeDischarge.Command.Start_NeredaController
Line01.Nereda02.Phase.Discharge.Command.Stop | Boolean |  |  |  |  | Line01.Nereda02 Phase Discharge Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.SludgeDischarge.Command.Stop_NeredaController
Line01.Nereda02.Phase.Feed.Command.Start | Boolean |  |  |  |  | Line01.Nereda02 Phase Feed Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Feed.Command.Start_NeredaController
Line01.Nereda02.Phase.Feed.Command.Stop | Boolean |  |  |  |  | Line01.Nereda02 Phase Feed Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Feed.Command.Stop_NeredaController
Line01.Nereda02.Phase.Feed.Control.FlowSetpoint | Float |  |  |  |  | Line01.Nereda02 feed flow setpoint |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.LogicFeed.IThis.Feed_Flow_SP
Line01.Nereda02.Phase.Vent.Command.Start | Boolean |  |  |  |  | Line01.Nereda02 Phase Vent Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Vent.Command.Start_NeredaController
Line01.Nereda02.Phase.Vent.Command.Stop | Boolean |  |  |  |  | Line01.Nereda02 Phase Vent Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Vent.Command.Stop_NeredaController
Line01.Nereda02.Phase.Vent.Control.AirGrid | Boolean |  |  |  |  | Line01.Nereda02 Vent air grid (diffusers) |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.LogicPhaseVent.IThis.VentAirGrid
Line01.Nereda02.Phase.Vent.Control.InfluentGrid | Boolean |  |  |  |  | Line01.Nereda02 Vent influent grid (feed pipes) |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.LogicPhaseVent.IThis.VentInfluentGrid
Line01.Nereda02.Phase.Wait.Command.Start | Boolean |  |  |  |  | Line01.Nereda02 Phase Wait Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Wait.Command.Start_NeredaController
Line01.Nereda02.Phase.Wait.Command.Stop | Boolean |  |  |  |  | Line01.Nereda02 Phase Wait Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.Reactorlogic.Wait.Command.Stop_NeredaController
Line01.Nereda02.Status | Integer |  |  |  |  | Line01.Nereda02 status for display on SCADA |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor02.IThis.Status
Line01.Nereda03.Phase.Aerate.Command.Start | Boolean |  |  |  |  | Line01.Nereda03 Phase Aerate Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Aerate.Command.Start_NeredaController
Line01.Nereda03.Phase.Aerate.Command.Stop | Boolean |  |  |  |  | Line01.Nereda03 Phase Aerate Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Aerate.Command.Stop_NeredaController
Line01.Nereda03.Phase.Aerate.Control.Capacity | Float |  |  |  |  | Line01.Nereda03 Required aeration capacity (0..100%) |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.LogicAerate.IThis.RunCapacity_Blower
Line01.Nereda03.Phase.Aerate.Control.AirGrid | Boolean |  |  |  |  | Line01.Nereda03 Aeration via air grid (diffusers) |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.LogicAerate.IThis.AerationGrid
Line01.Nereda03.Phase.Aerate.Control.InfluentGrid | Boolean |  |  |  |  | Line01.Nereda03 Aeration via influent grid (feed pipes) |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.LogicAerate.IThis.InfluentGrid
Line01.Nereda03.Phase.Discharge.Command.Start | Boolean |  |  |  |  | Line01.Nereda03 Phase Discharge Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.SludgeDischarge.Command.Start_NeredaController
Line01.Nereda03.Phase.Discharge.Command.Stop | Boolean |  |  |  |  | Line01.Nereda03 Phase Discharge Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.SludgeDischarge.Command.Stop_NeredaController
Line01.Nereda03.Phase.Feed.Command.Start | Boolean |  |  |  |  | Line01.Nereda03 Phase Feed Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Feed.Command.Start_NeredaController
Line01.Nereda03.Phase.Feed.Command.Stop | Boolean |  |  |  |  | Line01.Nereda03 Phase Feed Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Feed.Command.Stop_NeredaController
Line01.Nereda03.Phase.Feed.Control.FlowSetpoint | Float |  |  |  |  | Line01.Nereda03 feed flow setpoint |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.LogicFeed.IThis.Feed_Flow_SP
Line01.Nereda03.Phase.Vent.Command.Start | Boolean |  |  |  |  | Line01.Nereda03 Phase Vent Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Vent.Command.Start_NeredaController
Line01.Nereda03.Phase.Vent.Command.Stop | Boolean |  |  |  |  | Line01.Nereda03 Phase Vent Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Vent.Command.Stop_NeredaController
Line01.Nereda03.Phase.Vent.Control.AirGrid | Boolean |  |  |  |  | Line01.Nereda03 Vent air grid (diffusers) |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.LogicPhaseVent.IThis.VentAirGrid
Line01.Nereda03.Phase.Vent.Control.InfluentGrid | Boolean |  |  |  |  | Line01.Nereda03 Vent influent grid (feed pipes) |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.LogicPhaseVent.IThis.VentInfluentGrid
Line01.Nereda03.Phase.Wait.Command.Start | Boolean |  |  |  |  | Line01.Nereda03 Phase Wait Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Wait.Command.Start_NeredaController
Line01.Nereda03.Phase.Wait.Command.Stop | Boolean |  |  |  |  | Line01.Nereda03 Phase Wait Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.Reactorlogic.Wait.Command.Stop_NeredaController
Line01.Nereda03.Status | Integer |  |  |  |  | Line01.Nereda03 status for display on SCADA |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_Reactor03.IThis.Status
SludgeBuffer01.Phase.SB_Feed.Command.Start | Boolean |  |  |  |  | SludgeBuffer01 Phase Feed Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.Feed.Command.Start_NeredaController
SludgeBuffer01.Phase.SB_Feed.Command.Stop | Boolean |  |  |  |  | SludgeBuffer01 Phase Feed Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.Feed.Command.Stop_NeredaController
SludgeBuffer01.Phase.SB_SludgeDischarge.Command.Start | Boolean |  |  |  |  | SludgeBuffer01 Phase SludgeDischarge Start command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.SludgeDischarge.Command.Start_NeredaController
SludgeBuffer01.Phase.SB_SludgeDischarge.Command.Stop | Boolean |  |  |  |  | SludgeBuffer01 Phase SludgeDischarge Stop command from Nereda Controller |  |  |  | SoftdPAC_BX1_NVPP.RES0.NVPP_SludgeBuffer.SBLogic.SludgeDischarge.Command.Stop_NeredaController
SludgeBuffer01.Status | Integer |  |  |  |  | SludgeBuffer01 status for display on SCADA