## FromPLC
Nereda Tijuco Preto | Remarks
Interface list with signals that the Nereda controller reads from the PLC
BE1364
Version V2 31/07/2026 15:59:29
Signals from PLC | DataType | Address/ Register/ SQL/ TagName | Bit | Db | Freeze Signal | Error Signal | Scaling | Offset | Description
NeredaController.FieldStatus | Integer | [7 empty] | Nereda Controller numeric status (0= Off, 1= Manual, 2= Auto, -1= FallbackControl)
HeartBeat | Boolean | [7 empty] | Heartbeat signal from PLC to Nereda Controller
Influent.Signal.Flow | Float | [7 empty] | Flow from Pre-Treatment to Feed Buffer (40-FT-02)
Influent.Signal.ReturnFlow | Float | [7 empty] | Returns from C-press (900-FT-07)
Influent.Signal.Level | Float | [7 empty] | Radar level transmitter in the suction well of the raw sewage pumping station (100-LIT-03)
Influent.Signal.Level.Alarm | Boolean | [7 empty] | Radar level transmitter in the suction well of the raw sewage pumping station Alarm (100-LIT-03)
Influent.Signal.LevelSwitchLow | Float | [7 empty] | Level float switch for very low level control (100-LSL-04)
Influent.Signal.LevelSwitchHigh | Float | [7 empty] | Level float switch for very high level control (100-LSH-05)
Influent.Signal.Pressure | Float | [7 empty] | Pressure transmitter in the discharge line for control of the raw sewage discharge line (100-PT-01)
Influent.Signal.Pressure.Alarm | Boolean | [7 empty] | Pressure transmitter in the discharge line for control of the raw sewage discharge line Alarm (100-PT-01)
Influent.Equipment.Pump01.Run | Boolean | [7 empty] | Raw sewage pump 1 (100-BS-01) Status Run
Influent.Equipment.Pump01.Alarm | Boolean | [7 empty] | Raw sewage pump 1 (100-BS-01) Alarm
Influent.Equipment.Pump01.Mode | Boolean | [7 empty] | Raw sewage pump 1 (100-BS-01) Mode from SCADA (0=Manual, 1=Auto)
Influent.Equipment.Pump01.Frequency | Float | [7 empty] | Raw sewage pump 1 (100-BS-01) Frequency
Influent.Equipment.Pump01.Power | Float | [7 empty] | Raw sewage pump 1 (100-BS-01) Power (kW)
Influent.Equipment.Pump01.Capacity | Float | [7 empty] | Raw sewage pump 1 (100-BS-01) Capacity
Influent.Equipment.Pump02.Run | Boolean | [7 empty] | Raw sewage pump 2 (100-BS-02) Status Run
Influent.Equipment.Pump02.Alarm | Boolean | [7 empty] | Raw sewage pump 2 (100-BS-02) Alarm
Influent.Equipment.Pump02.Mode | Boolean | [7 empty] | Raw sewage pump 2 (100-BS-02) Mode from SCADA (0=Manual, 1=Auto)
Influent.Equipment.Pump02.Frequency | Float | [7 empty] | Raw sewage pump 2 (100-BS-02) Frequency
Influent.Equipment.Pump02.Power | Float | [7 empty] | Raw sewage pump 2 (100-BS-02) Power (kW)
Influent.Equipment.Pump02.Capacity | Float | [7 empty] | Raw sewage pump 2 (100-BS-02) Capacity
Influent.Equipment.Pump03.Run | Boolean | [7 empty] | Raw sewage pump 3 (100-BS-03) Status Run
Influent.Equipment.Pump03.Alarm | Boolean | [7 empty] | Raw sewage pump 3 (100-BS-03) Alarm
Influent.Equipment.Pump03.Mode | Boolean | [7 empty] | Raw sewage pump 3 (100-BS-03) Mode from SCADA (0=Manual, 1=Auto)
Influent.Equipment.Pump03.Frequency | Float | [7 empty] | Raw sewage pump 3 (100-BS-03) Frequency
Influent.Equipment.Pump03.Power | Float | [7 empty] | Raw sewage pump 3 (100-BS-03) Power (kW)
Influent.Equipment.Pump03.Capacity | Float | [7 empty] | Raw sewage pump 3 (100-BS-03) Capacity
Screens.Screen01.Signal.Level | Float | [7 empty] | Differential ultrasonic level meter upstream and downstream on the bar grid in Canal 1 EEE Final (101-LT-01)
Screens.Screen01.Signal.Level.Alarm | Boolean | [7 empty] | Differential ultrasonic level meter upstream and downstream on the bar grid in Canal 1 EEE Final Alarm (101-LT-01)
Screens.Screen02.Signal.Level | Float | [7 empty] | Differential ultrasonic level meter upstream and downstream on the bar grid in Canal 2 EEE Final (101-LT-02)
Screens.Screen02.Signal.Level.Alarm | Boolean | [7 empty] | Differential ultrasonic level meter upstream and downstream on the bar grid in Canal 2 EEE Final Alarm (101-LT-02)
Screens.Screen01.Before.Equipment.SluiceGate.Run | Boolean | [7 empty] | Sluice Gate in Canal 1 EEE Final Before Screw (100-CO-01) Status Run
Screens.Screen01.Before.Equipment.SluiceGate.Alarm | Boolean | [7 empty] | Sluice Gate in Canal 1 EEE Final Before Screw (100-CO-01) Alarm
Screens.Screen01.Before.Equipment.SluiceGate.Mode | Boolean | [7 empty] | Sluice Gate in Canal 1 EEE Final Before Screw (100-CO-01) Mode from SCADA (0=Manual, 1=Auto)
Screens.Screen01.Before.Equipment.SluiceGate.Frequency | Float | [7 empty] | Sluice Gate in Canal 1 EEE Final Before Screw (100-CO-01) Frequency
Screens.Screen01.Before.Equipment.SluiceGate.Power | Float | [7 empty] | Sluice Gate in Canal 1 EEE Final Before Screw (100-CO-01) Power (kW)
Screens.Screen01.Before.Equipment.SluiceGate.Capacity | Float | [7 empty] | Sluice Gate in Canal 1 EEE Final Before Screw (100-CO-01) Capacity
Screens.Screen02.Before.Equipment.SluiceGate.Run | Boolean | [7 empty] | Sluice Gate in Canal 2 EEE Final (100-CO-03) Status Run
Screens.Screen02.Before.Equipment.SluiceGate.Alarm | Boolean | [7 empty] | Sluice Gate in Canal 2 EEE Final (100-CO-03) Alarm
Screens.Screen02.Before.Equipment.SluiceGate.Mode | Boolean | [7 empty] | Sluice Gate in Canal 2 EEE Final (100-CO-03) Mode from SCADA (0=Manual, 1=Auto)
Screens.Screen02.Before.Equipment.SluiceGate.Frequency | Float | [7 empty] | Sluice Gate in Canal 2 EEE Final (100-CO-03) Frequency
Screens.Screen02.Before.Equipment.SluiceGate.Power | Float | [7 empty] | Sluice Gate in Canal 2 EEE Final (100-CO-03) Power (kW)
Screens.Screen02.Before.Equipment.SluiceGate.Capacity | Float | [7 empty] | Sluice Gate in Canal 2 EEE Final (100-CO-03) Capacity
Screens.Screen01.Equipment.Screen.Run | Boolean | [7 empty] | Bar grid with vertical mechanical cleaning Canal 1 (100-GM-01) Status Run
Screens.Screen01.Equipment.Screen.Alarm | Boolean | [7 empty] | Bar grid with vertical mechanical cleaning Canal 1 (100-GM-01) Alarm
Screens.Screen01.Equipment.Screen.Mode | Boolean | [7 empty] | Bar grid with vertical mechanical cleaning Canal 1 (100-GM-01) Mode from SCADA (0=Manual, 1=Auto)
Screens.Screen01.Equipment.Screen.Frequency | Float | [7 empty] | Bar grid with vertical mechanical cleaning Canal 1 (100-GM-01) Frequency
Screens.Screen01.Equipment.Screen.Power | Float | [7 empty] | Bar grid with vertical mechanical cleaning Canal 1 (100-GM-01) Power (kW)
Screens.Screen01.Equipment.Screen.Capacity | Float | [7 empty] | Bar grid with vertical mechanical cleaning Canal 1 (100-GM-01) Capacity
Screens.Screen02.Equipment.Screen.Run | Boolean | [7 empty] | Bar grid with vertical mechanical cleaning Canal 2 (100-GM-02) Status Run
Screens.Screen02.Equipment.Screen.Alarm | Boolean | [7 empty] | Bar grid with vertical mechanical cleaning Canal 2 (100-GM-02) Alarm
Screens.Screen02.Equipment.Screen.Mode | Boolean | [7 empty] | Bar grid with vertical mechanical cleaning Canal 2 (100-GM-02) Mode from SCADA (0=Manual, 1=Auto)
Screens.Screen02.Equipment.Screen.Frequency | Float | [7 empty] | Bar grid with vertical mechanical cleaning Canal 2 (100-GM-02) Frequency
Screens.Screen02.Equipment.Screen.Power | Float | [7 empty] | Bar grid with vertical mechanical cleaning Canal 2 (100-GM-02) Power (kW)
Screens.Screen02.Equipment.Screen.Capacity | Float | [7 empty] | Bar grid with vertical mechanical cleaning Canal 2 (100-GM-02) Capacity
Screens.Equipment.ScrewConveyor.Run | Boolean | [7 empty] | Screw Conveyor EEE Final (100-RT-01) Status Run
Screens.Equipment.ScrewConveyor.Alarm | Boolean | [7 empty] | Screw Conveyor EEE Final (100-RT-01) Alarm
Screens.Equipment.ScrewConveyor.Mode | Boolean | [7 empty] | Screw Conveyor EEE Final (100-RT-01) Mode from SCADA (0=Manual, 1=Auto)
Screens.Equipment.ScrewConveyor.Frequency | Float | [7 empty] | Screw Conveyor EEE Final (100-RT-01) Frequency
Screens.Equipment.ScrewConveyor.Power | Float | [7 empty] | Screw Conveyor EEE Final (100-RT-01) Power (kW)
Screens.Equipment.ScrewConveyor.Capacity | Float | [7 empty] | Screw Conveyor EEE Final (100-RT-01) Capacity
Screens.Screen01.After.Equipment.SluiceGate.Run | Boolean | [7 empty] | Sluice Gate in Canal 1 EEE Final After Screw (100-CO-02) Status Run
Screens.Screen01.After.Equipment.SluiceGate.Alarm | Boolean | [7 empty] | Sluice Gate in Canal 1 EEE Final After Screw (100-CO-02) Alarm
Screens.Screen01.After.Equipment.SluiceGate.Mode | Boolean | [7 empty] | Sluice Gate in Canal 1 EEE Final After Screw (100-CO-02) Mode from SCADA (0=Manual, 1=Auto)
Screens.Screen01.After.Equipment.SluiceGate.Frequency | Float | [7 empty] | Sluice Gate in Canal 1 EEE Final After Screw (100-CO-02) Frequency
Screens.Screen01.After.Equipment.SluiceGate.Power | Float | [7 empty] | Sluice Gate in Canal 1 EEE Final After Screw (100-CO-02) Power (kW)
Screens.Screen01.After.Equipment.SluiceGate.Capacity | Float | [7 empty] | Sluice Gate in Canal 1 EEE Final After Screw (100-CO-02) Capacity
Screens.Screen02.After.Equipment.SluiceGate.Run | Boolean | [7 empty] | Sluice Gate in Canal 2 EEE Final (100-CO-04) Status Run
Screens.Screen02.After.Equipment.SluiceGate.Alarm | Boolean | [7 empty] | Sluice Gate in Canal 2 EEE Final (100-CO-04) Alarm
Screens.Screen02.After.Equipment.SluiceGate.Mode | Boolean | [7 empty] | Sluice Gate in Canal 2 EEE Final (100-CO-04) Mode from SCADA (0=Manual, 1=Auto)
Screens.Screen02.After.Equipment.SluiceGate.Frequency | Float | [7 empty] | Sluice Gate in Canal 2 EEE Final (100-CO-04) Frequency
Screens.Screen02.After.Equipment.SluiceGate.Power | Float | [7 empty] | Sluice Gate in Canal 2 EEE Final (100-CO-04) Power (kW)
Screens.Screen02.After.Equipment.SluiceGate.Capacity | Float | [7 empty] | Sluice Gate in Canal 2 EEE Final (100-CO-04) Capacity
SandTrap.SandTrap01.Equipment.Preteatment.Run | Boolean | [7 empty] | Compact Pretreatment Unit 1 - First Stage (200-UTC-01) Status Run
SandTrap.SandTrap01.Equipment.Preteatment.Alarm | Boolean | [7 empty] | Compact Pretreatment Unit 1 - First Stage (200-UTC-01) Alarm
SandTrap.SandTrap01.Equipment.Preteatment.Mode | Boolean | [7 empty] | Compact Pretreatment Unit 1 - First Stage (200-UTC-01) Mode from SCADA (0=Manual, 1=Auto)
SandTrap.SandTrap01.Equipment.Preteatment.Frequency | Float | [7 empty] | Compact Pretreatment Unit 1 - First Stage (200-UTC-01) Frequency
SandTrap.SandTrap01.Equipment.Preteatment.Power | Float | [7 empty] | Compact Pretreatment Unit 1 - First Stage (200-UTC-01) Power (kW)
SandTrap.SandTrap01.Equipment.Preteatment.Capacity | Float | [7 empty] | Compact Pretreatment Unit 1 - First Stage (200-UTC-01) Capacity
SandTrap.SandTrap02.Equipment.Preteatment.Run | Boolean | [7 empty] | Compact Pretreatment Unit 2 - First Stage (200-UTC-02) Status Run
SandTrap.SandTrap02.Equipment.Preteatment.Alarm | Boolean | [7 empty] | Compact Pretreatment Unit 2 - First Stage (200-UTC-02) Alarm
SandTrap.SandTrap02.Equipment.Preteatment.Mode | Boolean | [7 empty] | Compact Pretreatment Unit 2 - First Stage (200-UTC-02) Mode from SCADA (0=Manual, 1=Auto)
SandTrap.SandTrap02.Equipment.Preteatment.Frequency | Float | [7 empty] | Compact Pretreatment Unit 2 - First Stage (200-UTC-02) Frequency
SandTrap.SandTrap02.Equipment.Preteatment.Power | Float | [7 empty] | Compact Pretreatment Unit 2 - First Stage (200-UTC-02) Power (kW)
SandTrap.SandTrap02.Equipment.Preteatment.Capacity | Float | [7 empty] | Compact Pretreatment Unit 2 - First Stage (200-UTC-02) Capacity
SandTrap.SandTrap03.Equipment.Preteatment.Run | Boolean | [7 empty] | Compact Pretreatment Unit 3 - Second Stage (200-UTC-03) Status Run
SandTrap.SandTrap03.Equipment.Preteatment.Alarm | Boolean | [7 empty] | Compact Pretreatment Unit 3 - Second Stage (200-UTC-03) Alarm
SandTrap.SandTrap03.Equipment.Preteatment.Mode | Boolean | [7 empty] | Compact Pretreatment Unit 3 - Second Stage (200-UTC-03) Mode from SCADA (0=Manual, 1=Auto)
SandTrap.SandTrap03.Equipment.Preteatment.Frequency | Float | [7 empty] | Compact Pretreatment Unit 3 - Second Stage (200-UTC-03) Frequency
SandTrap.SandTrap03.Equipment.Preteatment.Power | Float | [7 empty] | Compact Pretreatment Unit 3 - Second Stage (200-UTC-03) Power (kW)
SandTrap.SandTrap03.Equipment.Preteatment.Capacity | Float | [7 empty] | Compact Pretreatment Unit 3 - Second Stage (200-UTC-03) Capacity
SandTrap.SandTrap01.Equipment.Pump.Run | Boolean | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 1 (200-BR-03) Status Run
SandTrap.SandTrap01.Equipment.Pump.Alarm | Boolean | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 1 (200-BR-03) Alarm
SandTrap.SandTrap01.Equipment.Pump.Mode | Boolean | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 1 (200-BR-03) Mode from SCADA (0=Manual, 1=Auto)
SandTrap.SandTrap01.Equipment.Pump.Frequency | Float | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 1 (200-BR-03) Frequency
SandTrap.SandTrap01.Equipment.Pump.Power | Float | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 1 (200-BR-03) Power (kW)
SandTrap.SandTrap01.Equipment.Pump.Capacity | Float | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 1 (200-BR-03) Capacity
SandTrap.SandTrap02.Equipment.Pump.Run | Boolean | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 2 (200-BR-04) Status Run
SandTrap.SandTrap02.Equipment.Pump.Alarm | Boolean | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 2 (200-BR-04) Alarm
SandTrap.SandTrap02.Equipment.Pump.Mode | Boolean | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 2 (200-BR-04) Mode from SCADA (0=Manual, 1=Auto)
SandTrap.SandTrap02.Equipment.Pump.Frequency | Float | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 2 (200-BR-04) Frequency
SandTrap.SandTrap02.Equipment.Pump.Power | Float | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 2 (200-BR-04) Power (kW)
SandTrap.SandTrap02.Equipment.Pump.Capacity | Float | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 2 (200-BR-04) Capacity
SandTrap.SandTrap03.Equipment.Pump.Run | Boolean | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 3 (200-BR-05) Status Run
SandTrap.SandTrap03.Equipment.Pump.Alarm | Boolean | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 3 (200-BR-05) Alarm
SandTrap.SandTrap03.Equipment.Pump.Mode | Boolean | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 3 (200-BR-05) Mode from SCADA (0=Manual, 1=Auto)
SandTrap.SandTrap03.Equipment.Pump.Frequency | Float | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 3 (200-BR-05) Frequency
SandTrap.SandTrap03.Equipment.Pump.Power | Float | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 3 (200-BR-05) Power (kW)
SandTrap.SandTrap03.Equipment.Pump.Capacity | Float | [7 empty] | Helical pressure pump for removing grease form the pretreatment unit Pretreatment Unit 3 (200-BR-05) Capacity
Effluent.Equipment.Valve.Open | Boolean | [7 empty] | Modulating valve for flow control, Open status (700-VC-01)
Effluent.Equipment.Valve.Closed | Boolean | [7 empty] | Modulating valve for flow control, Closed status (700-VC-01)
Effluent.Equipment.Valve.Alarm | Boolean | [7 empty] | Modulating valve for flow control, Alarm status (700-VC-01)
Effluent.Equipment.Valve.Mode | Boolean | [7 empty] | Modulating valve for flow control (700-VC-01) Mode from SCADA (0=Manual, 1=Auto)
Effluent.Signal.LevelSwitchLow01 | Float | [7 empty] | Low-level switch in disinfection channel 1, supplied with the disinfection system (700-LSL-01)
Effluent.Signal.LevelSwitchLow02 | Float | [7 empty] | Low-level switch in disinfection channel 2, supplied with the disinfection system (700-LSL-02)
Effluent.Signal.Flow | Float | [7 empty] | Flow meter in a Parshall flume for treated effluent (700-FT-01)
Effluent.Signal.Flow.Alarm | Boolean | [7 empty] | Flow meter in a Parshall flume for treated effluent Alarm (700-FT-01)
Effluent.Signal.Turbidity | Float | [7 empty] | Turbidity analyzer at the treated effluent outlet, with local display (40-QT-2101)
Effluent.Signal.Turbidity.Alarm | Boolean | [7 empty] | Turbidity analyzer at the treated effluent outlet, with local display Alarm (40-QT-2101)
Aeration.Equipment.AirCompressor01.Run | Boolean | [7 empty] | Air compressor 1 for suplying air to control valves (500-COMP-01) Status Run
Aeration.Equipment.AirCompressor01.Alarm | Boolean | [7 empty] | Air compressor 1 for suplying air to control valves (500-COMP-01) Alarm
Aeration.Equipment.AirCompressor01.Mode | Boolean | [7 empty] | Air compressor 1 for suplying air to control valves (500-COMP-01) Mode from SCADA (0=Manual, 1=Auto)
Aeration.Equipment.AirCompressor01.Frequency | Float | [7 empty] | Air compressor 1 for suplying air to control valves (500-COMP-01) Frequency
Aeration.Equipment.AirCompressor01.Power | Float | [7 empty] | Air compressor 1 for suplying air to control valves (500-COMP-01) Power (kW)
Aeration.Equipment.AirCompressor01.Capacity | Float | [7 empty] | Air compressor 1 for suplying air to control valves (500-COMP-01) Capacity
Aeration.Equipment.AirCompressor02.Run | Boolean | [7 empty] | Air compressor 2 for suplying air to control valves (500-COMP-02) Status Run
Aeration.Equipment.AirCompressor02.Alarm | Boolean | [7 empty] | Air compressor 2 for suplying air to control valves (500-COMP-02) Alarm
Aeration.Equipment.AirCompressor02.Mode | Boolean | [7 empty] | Air compressor 2 for suplying air to control valves (500-COMP-02) Mode from SCADA (0=Manual, 1=Auto)
Aeration.Equipment.AirCompressor02.Frequency | Float | [7 empty] | Air compressor 2 for suplying air to control valves (500-COMP-02) Frequency
Aeration.Equipment.AirCompressor02.Power | Float | [7 empty] | Air compressor 2 for suplying air to control valves (500-COMP-02) Power (kW)
Aeration.Equipment.AirCompressor02.Capacity | Float | [7 empty] | Air compressor 2 for suplying air to control valves (500-COMP-02) Capacity
Aeration.Equipment.Blower01.Run | Boolean | [7 empty] | Air Blower 1 (V-4601) Status Run
Aeration.Equipment.Blower01.Alarm | Boolean | [7 empty] | Air Blower 1 (V-4601) Alarm
Aeration.Equipment.Blower01.Mode | Boolean | [7 empty] | Air Blower 1 (V-4601) Mode from SCADA (0=Manual, 1=Auto)
Aeration.Equipment.Blower01.Frequency | Float | [7 empty] | Air Blower 1 (V-4601) Frequency
Aeration.Equipment.Blower01.Power | Float | [7 empty] | Air Blower 1 (V-4601) Power (kW)
Aeration.Equipment.Blower01.Capacity | Float | [7 empty] | Air Blower 1 (V-4601) Capacity
Aeration.Equipment.Blower02.Run | Boolean | [7 empty] | Air Blower 2 (V-4602) Status Run
Aeration.Equipment.Blower02.Alarm | Boolean | [7 empty] | Air Blower 2 (V-4602) Alarm
Aeration.Equipment.Blower02.Mode | Boolean | [7 empty] | Air Blower 2 (V-4602) Mode from SCADA (0=Manual, 1=Auto)
Aeration.Equipment.Blower02.Frequency | Float | [7 empty] | Air Blower 2 (V-4602) Frequency
Aeration.Equipment.Blower02.Power | Float | [7 empty] | Air Blower 2 (V-4602) Power (kW)
Aeration.Equipment.Blower02.Capacity | Float | [7 empty] | Air Blower 2 (V-4602) Capacity
Aeration.Equipment.Blower03.Run | Boolean | [7 empty] | Air Blower 3 (V-4603) Status Run
Aeration.Equipment.Blower03.Alarm | Boolean | [7 empty] | Air Blower 3 (V-4603) Alarm
Aeration.Equipment.Blower03.Mode | Boolean | [7 empty] | Air Blower 3 (V-4603) Mode from SCADA (0=Manual, 1=Auto)
Aeration.Equipment.Blower03.Frequency | Float | [7 empty] | Air Blower 3 (V-4603) Frequency
Aeration.Equipment.Blower03.Power | Float | [7 empty] | Air Blower 3 (V-4603) Power (kW)
Aeration.Equipment.Blower03.Capacity | Float | [7 empty] | Air Blower 3 (V-4603) Capacity
Aeration.Equipment.Blower04.Run | Boolean | [7 empty] | Air Blower 4 (V-4604) Status Run
Aeration.Equipment.Blower04.Alarm | Boolean | [7 empty] | Air Blower 4 (V-4604) Alarm
Aeration.Equipment.Blower04.Mode | Boolean | [7 empty] | Air Blower 4 (V-4604) Mode from SCADA (0=Manual, 1=Auto)
Aeration.Equipment.Blower04.Frequency | Float | [7 empty] | Air Blower 4 (V-4604) Frequency
Aeration.Equipment.Blower04.Power | Float | [7 empty] | Air Blower 4 (V-4604) Power (kW)
Aeration.Equipment.Blower04.Capacity | Float | [7 empty] | Air Blower 4 (V-4604) Capacity
Aeration.Equipment.BlowerValve01.Open | Boolean | [7 empty] | Pneumatic butterfly valve at the outlet of the V4601 blower pipe, Open status (AV-46-012)
Aeration.Equipment.BlowerValve01.Closed | Boolean | [7 empty] | Pneumatic butterfly valve at the outlet of the V4601 blower pipe, Closed status (AV-46-012)
Aeration.Equipment.BlowerValve01.Alarm | Boolean | [7 empty] | Pneumatic butterfly valve at the outlet of the V4601 blower pipe, Alarm status (AV-46-012)
Aeration.Equipment.BlowerValve01.Mode | Boolean | [7 empty] | Pneumatic butterfly valve at the outlet of the V4601 blower pipe (AV-46-012) Mode from SCADA (0=Manual, 1=Auto)
Aeration.Equipment.BlowerValve02.Open | Boolean | [7 empty] | Pneumatic butterfly valve at the outlet of the V4602 blower pipe, Open status (AV-46-022)
Aeration.Equipment.BlowerValve02.Closed | Boolean | [7 empty] | Pneumatic butterfly valve at the outlet of the V4602 blower pipe, Closed status (AV-46-022)
Aeration.Equipment.BlowerValve02.Alarm | Boolean | [7 empty] | Pneumatic butterfly valve at the outlet of the V4602 blower pipe, Alarm status (AV-46-022)
Aeration.Equipment.BlowerValve02.Mode | Boolean | [7 empty] | Pneumatic butterfly valve at the outlet of the V4602 blower pipe (AV-46-022) Mode from SCADA (0=Manual, 1=Auto)
Aeration.Equipment.BlowerValve03.Open | Boolean | [7 empty] | Pneumatic butterfly valve at the outlet of the V4603 blower pipe, Open status (AV-46-032)
Aeration.Equipment.BlowerValve03.Closed | Boolean | [7 empty] | Pneumatic butterfly valve at the outlet of the V4603 blower pipe, Closed status (AV-46-032)
Aeration.Equipment.BlowerValve03.Alarm | Boolean | [7 empty] | Pneumatic butterfly valve at the outlet of the V4603 blower pipe, Alarm status (AV-46-032)
Aeration.Equipment.BlowerValve03.Mode | Boolean | [7 empty] | Pneumatic butterfly valve at the outlet of the V4603 blower pipe (AV-46-032) Mode from SCADA (0=Manual, 1=Auto)
Aeration.Equipment.BlowerValve04.Open | Boolean | [7 empty] | Pneumatic butterfly valve at the outlet of the V4604 blower pipe, Open status (AV-46-042)
Aeration.Equipment.BlowerValve04.Closed | Boolean | [7 empty] | Pneumatic butterfly valve at the outlet of the V4604 blower pipe, Closed status (AV-46-042)
Aeration.Equipment.BlowerValve04.Alarm | Boolean | [7 empty] | Pneumatic butterfly valve at the outlet of the V4604 blower pipe, Alarm status (AV-46-042)
Aeration.Equipment.BlowerValve04.Mode | Boolean | [7 empty] | Pneumatic butterfly valve at the outlet of the V4604 blower pipe (AV-46-042) Mode from SCADA (0=Manual, 1=Auto)
Aeration.Equipment.HeaderSelectionValve01.Open | Boolean | [7 empty] | Pneumatic butterfly valve in the pipingconnecting blower V4601 and blower V4602, Open status (AV-46-001)
Aeration.Equipment.HeaderSelectionValve01.Closed | Boolean | [7 empty] | Pneumatic butterfly valve in the pipingconnecting blower V4601 and blower V4602, Closed status (AV-46-001)
Aeration.Equipment.HeaderSelectionValve01.Alarm | Boolean | [7 empty] | Pneumatic butterfly valve in the pipingconnecting blower V4601 and blower V4602, Alarm status (AV-46-001)
Aeration.Equipment.HeaderSelectionValve01.Mode | Boolean | [7 empty] | Pneumatic butterfly valve in the pipingconnecting blower V4601 and blower V4602 (AV-46-001) Mode from SCADA (0=Manual, 1=Auto)
Aeration.Equipment.HeaderSelectionValve02.Open | Boolean | [7 empty] | Pneumatic butterfly valve in the piping connecting blower V4602 and blower V4603, Open status (AV-46-002)
Aeration.Equipment.HeaderSelectionValve02.Closed | Boolean | [7 empty] | Pneumatic butterfly valve in the piping connecting blower V4602 and blower V4603, Closed status (AV-46-002)
Aeration.Equipment.HeaderSelectionValve02.Alarm | Boolean | [7 empty] | Pneumatic butterfly valve in the piping connecting blower V4602 and blower V4603, Alarm status (AV-46-002)
Aeration.Equipment.HeaderSelectionValve02.Mode | Boolean | [7 empty] | Pneumatic butterfly valve in the piping connecting blower V4602 and blower V4603 (AV-46-002) Mode from SCADA (0=Manual, 1=Auto)
Aeration.Equipment.HeaderSelectionValve03.Open | Boolean | [7 empty] | Pneumatic butterfly valve in the piping connecting blower V4603 and blower V4604, Open status (AV-46-003)
Aeration.Equipment.HeaderSelectionValve03.Closed | Boolean | [7 empty] | Pneumatic butterfly valve in the piping connecting blower V4603 and blower V4604, Closed status (AV-46-003)
Aeration.Equipment.HeaderSelectionValve03.Alarm | Boolean | [7 empty] | Pneumatic butterfly valve in the piping connecting blower V4603 and blower V4604, Alarm status (AV-46-003)
Aeration.Equipment.HeaderSelectionValve03.Mode | Boolean | [7 empty] | Pneumatic butterfly valve in the piping connecting blower V4603 and blower V4604 (AV-46-003) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.SludgeHoldingTank01.Signal.Level | Float | [7 empty] | Level gauge in the sludge storage tank 1 (900-LIT-01)
SludgeTreatment.SludgeHoldingTank01.Signal.Level.Alarm | Boolean | [7 empty] | Level gauge in the sludge storage tank 1 Alarm (900-LIT-01)
SludgeTreatment.SludgeHoldingTank02.Signal.Level | Float | [7 empty] | Level gauge in the sludge storage tank 2 (900-LIT-02)
SludgeTreatment.SludgeHoldingTank02.Signal.Level.Alarm | Boolean | [7 empty] | Level gauge in the sludge storage tank 2 Alarm (900-LIT-02)
SludgeTreatment.SludgeTransferPumps.Signal.Flow01 | Float | [7 empty] | Electromagnetic flow meter in the sludge discharge line of pump 900-BO-01 (900-FT-01)
SludgeTreatment.SludgeTransferPumps.Signal.Flow01.Alarm | Boolean | [7 empty] | Electromagnetic flow meter in the sludge discharge line of pump 900-BO-01 Alarm (900-FT-01)
SludgeTreatment.SludgeTransferPumps.Signal.Flow02 | Float | [7 empty] | Electromagnetic flow meter in the sludge discharge line of pump 900-BO-02 (900-FT-02)
SludgeTreatment.SludgeTransferPumps.Signal.Flow02.Alarm | Boolean | [7 empty] | Electromagnetic flow meter in the sludge discharge line of pump 900-BO-02 Alarm (900-FT-02)
SludgeTreatment.SludgeTransferPumps.Signal.Flow03 | Float | [7 empty] | Electromagnetic flow meter in the sludge discharge line of pump 900-BO-03 (900-FT-03)
SludgeTreatment.SludgeTransferPumps.Signal.Flow03.Alarm | Boolean | [7 empty] | Electromagnetic flow meter in the sludge discharge line of pump 900-BO-03 Alarm (900-FT-03)
SludgeTreatment.SludgeHoldingTank01.Equipment.Valve01.Open | Boolean | [7 empty] | Pneumatic gate valve for controlling slurry flow to storage tank 1, Open status (AV-49-004)
SludgeTreatment.SludgeHoldingTank01.Equipment.Valve01.Closed | Boolean | [7 empty] | Pneumatic gate valve for controlling slurry flow to storage tank 1, Closed status (AV-49-004)
SludgeTreatment.SludgeHoldingTank01.Equipment.Valve01.Alarm | Boolean | [7 empty] | Pneumatic gate valve for controlling slurry flow to storage tank 1, Alarm status (AV-49-004)
SludgeTreatment.SludgeHoldingTank01.Equipment.Valve01.Mode | Boolean | [7 empty] | Pneumatic gate valve for controlling slurry flow to storage tank 1 (AV-49-004) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.SludgeHoldingTank02.Equipment.Valve01.Open | Boolean | [7 empty] | Pneumatic gate valve for controlling slurry flow to storage tank 2, Open status (AV-49-005)
SludgeTreatment.SludgeHoldingTank02.Equipment.Valve01.Closed | Boolean | [7 empty] | Pneumatic gate valve for controlling slurry flow to storage tank 2, Closed status (AV-49-005)
SludgeTreatment.SludgeHoldingTank02.Equipment.Valve01.Alarm | Boolean | [7 empty] | Pneumatic gate valve for controlling slurry flow to storage tank 2, Alarm status (AV-49-005)
SludgeTreatment.SludgeHoldingTank02.Equipment.Valve01.Mode | Boolean | [7 empty] | Pneumatic gate valve for controlling slurry flow to storage tank 2 (AV-49-005) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.SludgeHoldingTank01.Equipment.Valve02.Open | Boolean | [7 empty] | Motorized valve at the outlet of sludge storage tank 1, Open status (900-VA-01)
SludgeTreatment.SludgeHoldingTank01.Equipment.Valve02.Closed | Boolean | [7 empty] | Motorized valve at the outlet of sludge storage tank 1, Closed status (900-VA-01)
SludgeTreatment.SludgeHoldingTank01.Equipment.Valve02.Alarm | Boolean | [7 empty] | Motorized valve at the outlet of sludge storage tank 1, Alarm status (900-VA-01)
SludgeTreatment.SludgeHoldingTank01.Equipment.Valve02.Mode | Boolean | [7 empty] | Motorized valve at the outlet of sludge storage tank 1 (900-VA-01) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.SludgeHoldingTank02.Equipment.Valve02.Open | Boolean | [7 empty] | Motorized valve at the outlet of sludge storage tank 2, Open status (900-VA-02)
SludgeTreatment.SludgeHoldingTank02.Equipment.Valve02.Closed | Boolean | [7 empty] | Motorized valve at the outlet of sludge storage tank 2, Closed status (900-VA-02)
SludgeTreatment.SludgeHoldingTank02.Equipment.Valve02.Alarm | Boolean | [7 empty] | Motorized valve at the outlet of sludge storage tank 2, Alarm status (900-VA-02)
SludgeTreatment.SludgeHoldingTank02.Equipment.Valve02.Mode | Boolean | [7 empty] | Motorized valve at the outlet of sludge storage tank 2 (900-VA-02) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.SludgeHoldingTank01.Equipment.Blower.Run | Boolean | [7 empty] | Blower 1 for sludge storage tanks (900-SO-01) Status Run
SludgeTreatment.SludgeHoldingTank01.Equipment.Blower.Alarm | Boolean | [7 empty] | Blower 1 for sludge storage tanks (900-SO-01) Alarm
SludgeTreatment.SludgeHoldingTank01.Equipment.Blower.Mode | Boolean | [7 empty] | Blower 1 for sludge storage tanks (900-SO-01) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.SludgeHoldingTank01.Equipment.Blower.Frequency | Float | [7 empty] | Blower 1 for sludge storage tanks (900-SO-01) Frequency
SludgeTreatment.SludgeHoldingTank01.Equipment.Blower.Power | Float | [7 empty] | Blower 1 for sludge storage tanks (900-SO-01) Power (kW)
SludgeTreatment.SludgeHoldingTank01.Equipment.Blower.Capacity | Float | [7 empty] | Blower 1 for sludge storage tanks (900-SO-01) Capacity
SludgeTreatment.SludgeHoldingTank02.Equipment.Blower.Run | Boolean | [7 empty] | Blower 2 for sludge storage tanks (900-SO-02) Status Run
SludgeTreatment.SludgeHoldingTank02.Equipment.Blower.Alarm | Boolean | [7 empty] | Blower 2 for sludge storage tanks (900-SO-02) Alarm
SludgeTreatment.SludgeHoldingTank02.Equipment.Blower.Mode | Boolean | [7 empty] | Blower 2 for sludge storage tanks (900-SO-02) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.SludgeHoldingTank02.Equipment.Blower.Frequency | Float | [7 empty] | Blower 2 for sludge storage tanks (900-SO-02) Frequency
SludgeTreatment.SludgeHoldingTank02.Equipment.Blower.Power | Float | [7 empty] | Blower 2 for sludge storage tanks (900-SO-02) Power (kW)
SludgeTreatment.SludgeHoldingTank02.Equipment.Blower.Capacity | Float | [7 empty] | Blower 2 for sludge storage tanks (900-SO-02) Capacity
SludgeTreatment.Equipment.SludgeTransferPump01.Run | Boolean | [7 empty] | Sludge transfer pump 1 for transferring sludge to the thickening system (900-BO-01) Status Run
SludgeTreatment.Equipment.SludgeTransferPump01.Alarm | Boolean | [7 empty] | Sludge transfer pump 1 for transferring sludge to the thickening system (900-BO-01) Alarm
SludgeTreatment.Equipment.SludgeTransferPump01.Mode | Boolean | [7 empty] | Sludge transfer pump 1 for transferring sludge to the thickening system (900-BO-01) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.Equipment.SludgeTransferPump01.Frequency | Float | [7 empty] | Sludge transfer pump 1 for transferring sludge to the thickening system (900-BO-01) Frequency
SludgeTreatment.Equipment.SludgeTransferPump01.Power | Float | [7 empty] | Sludge transfer pump 1 for transferring sludge to the thickening system (900-BO-01) Power (kW)
SludgeTreatment.Equipment.SludgeTransferPump01.Capacity | Float | [7 empty] | Sludge transfer pump 1 for transferring sludge to the thickening system (900-BO-01) Capacity
SludgeTreatment.Equipment.SludgeTransferPump02.Run | Boolean | [7 empty] | Sludge transfer pump 2 for transferring sludge to the thickening system (900-BO-02) Status Run
SludgeTreatment.Equipment.SludgeTransferPump02.Alarm | Boolean | [7 empty] | Sludge transfer pump 2 for transferring sludge to the thickening system (900-BO-02) Alarm
SludgeTreatment.Equipment.SludgeTransferPump02.Mode | Boolean | [7 empty] | Sludge transfer pump 2 for transferring sludge to the thickening system (900-BO-02) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.Equipment.SludgeTransferPump02.Frequency | Float | [7 empty] | Sludge transfer pump 2 for transferring sludge to the thickening system (900-BO-02) Frequency
SludgeTreatment.Equipment.SludgeTransferPump02.Power | Float | [7 empty] | Sludge transfer pump 2 for transferring sludge to the thickening system (900-BO-02) Power (kW)
SludgeTreatment.Equipment.SludgeTransferPump02.Capacity | Float | [7 empty] | Sludge transfer pump 2 for transferring sludge to the thickening system (900-BO-02) Capacity
SludgeTreatment.Equipment.SludgeTransferPump03.Run | Boolean | [7 empty] | Sludge transfer pump 3 for transferring sludge to the thickening system (900-BO-03) Status Run
SludgeTreatment.Equipment.SludgeTransferPump03.Alarm | Boolean | [7 empty] | Sludge transfer pump 3 for transferring sludge to the thickening system (900-BO-03) Alarm
SludgeTreatment.Equipment.SludgeTransferPump03.Mode | Boolean | [7 empty] | Sludge transfer pump 3 for transferring sludge to the thickening system (900-BO-03) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.Equipment.SludgeTransferPump03.Frequency | Float | [7 empty] | Sludge transfer pump 3 for transferring sludge to the thickening system (900-BO-03) Frequency
SludgeTreatment.Equipment.SludgeTransferPump03.Power | Float | [7 empty] | Sludge transfer pump 3 for transferring sludge to the thickening system (900-BO-03) Power (kW)
SludgeTreatment.Equipment.SludgeTransferPump03.Capacity | Float | [7 empty] | Sludge transfer pump 3 for transferring sludge to the thickening system (900-BO-03) Capacity
SludgeTreatment.SludgeTransferPump01.Equipment.Valve.Open | Boolean | [7 empty] | Motorized valve downstream of the booster pump 900-BO-01, Open status (900-VA-06)
SludgeTreatment.SludgeTransferPump01.Equipment.Valve.Closed | Boolean | [7 empty] | Motorized valve downstream of the booster pump 900-BO-01, Closed status (900-VA-06)
SludgeTreatment.SludgeTransferPump01.Equipment.Valve.Alarm | Boolean | [7 empty] | Motorized valve downstream of the booster pump 900-BO-01, Alarm status (900-VA-06)
SludgeTreatment.SludgeTransferPump01.Equipment.Valve.Mode | Boolean | [7 empty] | Motorized valve downstream of the booster pump 900-BO-01 (900-VA-06) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.SludgeTransferPump02.Equipment.Valve.Open | Boolean | [7 empty] | Motorized valve downstream of the booster pump 900-BO-02, Open status (900-VA-07)
SludgeTreatment.SludgeTransferPump02.Equipment.Valve.Closed | Boolean | [7 empty] | Motorized valve downstream of the booster pump 900-BO-02, Closed status (900-VA-07)
SludgeTreatment.SludgeTransferPump02.Equipment.Valve.Alarm | Boolean | [7 empty] | Motorized valve downstream of the booster pump 900-BO-02, Alarm status (900-VA-07)
SludgeTreatment.SludgeTransferPump02.Equipment.Valve.Mode | Boolean | [7 empty] | Motorized valve downstream of the booster pump 900-BO-02 (900-VA-07) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.SludgeTransferPump03.Equipment.Valve.Open | Boolean | [7 empty] | Motorized valve downstream of the booster pump 900-BO-03, Open status (900-VA-08)
SludgeTreatment.SludgeTransferPump03.Equipment.Valve.Closed | Boolean | [7 empty] | Motorized valve downstream of the booster pump 900-BO-03, Closed status (900-VA-08)
SludgeTreatment.SludgeTransferPump03.Equipment.Valve.Alarm | Boolean | [7 empty] | Motorized valve downstream of the booster pump 900-BO-03, Alarm status (900-VA-08)
SludgeTreatment.SludgeTransferPump03.Equipment.Valve.Mode | Boolean | [7 empty] | Motorized valve downstream of the booster pump 900-BO-03 (900-VA-08) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve01.Open | Boolean | [7 empty] | Motorized valve in the junction chamber of the sludge booster pumps, Open status (900-VA-09)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve01.Closed | Boolean | [7 empty] | Motorized valve in the junction chamber of the sludge booster pumps, Closed status (900-VA-09)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve01.Alarm | Boolean | [7 empty] | Motorized valve in the junction chamber of the sludge booster pumps, Alarm status (900-VA-09)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve01.Mode | Boolean | [7 empty] | Motorized valve in the junction chamber of the sludge booster pumps (900-VA-09) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve02.Open | Boolean | [7 empty] | Motorized valve in the junction chamber of the sludge booster pumps, Open status (900-VA-10)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve02.Closed | Boolean | [7 empty] | Motorized valve in the junction chamber of the sludge booster pumps, Closed status (900-VA-10)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve02.Alarm | Boolean | [7 empty] | Motorized valve in the junction chamber of the sludge booster pumps, Alarm status (900-VA-10)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve02.Mode | Boolean | [7 empty] | Motorized valve in the junction chamber of the sludge booster pumps (900-VA-10) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve03.Open | Boolean | [7 empty] | Motorized valve in the discharge line of the C-Press 900-AD-01, Open status (900-VA-11)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve03.Closed | Boolean | [7 empty] | Motorized valve in the discharge line of the C-Press 900-AD-01, Closed status (900-VA-11)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve03.Alarm | Boolean | [7 empty] | Motorized valve in the discharge line of the C-Press 900-AD-01, Alarm status (900-VA-11)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve03.Mode | Boolean | [7 empty] | Motorized valve in the discharge line of the C-Press 900-AD-01 (900-VA-11) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve04.Open | Boolean | [7 empty] | Motorized valve in the discharge line of the C-Press 900-AD-02, Open status (900-VA-12)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve04.Closed | Boolean | [7 empty] | Motorized valve in the discharge line of the C-Press 900-AD-02, Closed status (900-VA-12)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve04.Alarm | Boolean | [7 empty] | Motorized valve in the discharge line of the C-Press 900-AD-02, Alarm status (900-VA-12)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve04.Mode | Boolean | [7 empty] | Motorized valve in the discharge line of the C-Press 900-AD-02 (900-VA-12) Mode from SCADA (0=Manual, 1=Auto)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve05.Open | Boolean | [7 empty] | Motorized valve in the discharge line of the C-Press 900-AD-03, Open status (900-VA-13)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve05.Closed | Boolean | [7 empty] | Motorized valve in the discharge line of the C-Press 900-AD-03, Closed status (900-VA-13)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve05.Alarm | Boolean | [7 empty] | Motorized valve in the discharge line of the C-Press 900-AD-03, Alarm status (900-VA-13)
SludgeTreatment.SludgeTransferPumps.Equipment.Valve05.Mode | Boolean | [7 empty] | Motorized valve in the discharge line of the C-Press 900-AD-03 (900-VA-13) Mode from SCADA (0=Manual, 1=Auto)
Chemicals.MetalDosing.Equipment.DosingPump01.Run | Boolean | [7 empty] | Caustic soda transfer pump (800-BO-02) Status Run
Chemicals.MetalDosing.Equipment.DosingPump01.Alarm | Boolean | [7 empty] | Caustic soda transfer pump (800-BO-02) Alarm
Chemicals.MetalDosing.Equipment.DosingPump01.Mode | Boolean | [7 empty] | Caustic soda transfer pump (800-BO-02) Mode from SCADA (0=Manual, 1=Auto)
Chemicals.MetalDosing.Equipment.DosingPump01.Frequency | Float | [7 empty] | Caustic soda transfer pump (800-BO-02) Frequency
Chemicals.MetalDosing.Equipment.DosingPump01.Power | Float | [7 empty] | Caustic soda transfer pump (800-BO-02) Power (kW)
Chemicals.MetalDosing.Equipment.DosingPump01.Capacity | Float | [7 empty] | Caustic soda transfer pump (800-BO-02) Capacity
Chemicals.MetalDosing.Equipment.DosingPump02.Run | Boolean | [7 empty] | Single-phase metering pump for dosing (800-DO-04) Status Run
Chemicals.MetalDosing.Equipment.DosingPump02.Alarm | Boolean | [7 empty] | Single-phase metering pump for dosing (800-DO-04) Alarm
Chemicals.MetalDosing.Equipment.DosingPump02.Mode | Boolean | [7 empty] | Single-phase metering pump for dosing (800-DO-04) Mode from SCADA (0=Manual, 1=Auto)
Chemicals.MetalDosing.Equipment.DosingPump02.Frequency | Float | [7 empty] | Single-phase metering pump for dosing (800-DO-04) Frequency
Chemicals.MetalDosing.Equipment.DosingPump02.Power | Float | [7 empty] | Single-phase metering pump for dosing (800-DO-04) Power (kW)
Chemicals.MetalDosing.Equipment.DosingPump02.Capacity | Float | [7 empty] | Single-phase metering pump for dosing (800-DO-04) Capacity
Chemicals.MetalDosing.Equipment.DosingPump03.Run | Boolean | [7 empty] | Single-phase metering pump for dosing (800-DO-05) Status Run
Chemicals.MetalDosing.Equipment.DosingPump03.Alarm | Boolean | [7 empty] | Single-phase metering pump for dosing (800-DO-05) Alarm
Chemicals.MetalDosing.Equipment.DosingPump03.Mode | Boolean | [7 empty] | Single-phase metering pump for dosing (800-DO-05) Mode from SCADA (0=Manual, 1=Auto)
Chemicals.MetalDosing.Equipment.DosingPump03.Frequency | Float | [7 empty] | Single-phase metering pump for dosing (800-DO-05) Frequency
Chemicals.MetalDosing.Equipment.DosingPump03.Power | Float | [7 empty] | Single-phase metering pump for dosing (800-DO-05) Power (kW)
Chemicals.MetalDosing.Equipment.DosingPump03.Capacity | Float | [7 empty] | Single-phase metering pump for dosing (800-DO-05) Capacity
Chemicals.MetalDosing.Signal.Level | Float | [7 empty] | Level in Alkalizing tank (800-LIT-03)
Chemicals.MetalDosing.Signal.Level.Alarm | Boolean | [7 empty] | Level in Alkalizing tank Alarm (800-LIT-03)
Chemicals.PolymerDosing.Signal.Flow01 | Float | [7 empty] | Electromagnetic flow meter in the polymer feed line for the C-Press 900-AD-01 (900-FT-04)
Chemicals.PolymerDosing.Signal.Flow01.Alarm | Boolean | [7 empty] | Electromagnetic flow meter in the polymer feed line for the C-Press 900-AD-01 Alarm (900-FT-04)
Chemicals.PolymerDosing.Signal.Flow02 | Float | [7 empty] | Electromagnetic flow meter in the polymer feed line for the C-Press 900-AD-02 (900-FT-05)
Chemicals.PolymerDosing.Signal.Flow02.Alarm | Boolean | [7 empty] | Electromagnetic flow meter in the polymer feed line for the C-Press 900-AD-02 Alarm (900-FT-05)
Chemicals.PolymerDosing.Signal.Flow03 | Float | [7 empty] | Electromagnetic flow meter in the polymer feed line for the C-Press 900-AD-03 (900-FT-06)
Chemicals.PolymerDosing.Signal.Flow03.Alarm | Boolean | [7 empty] | Electromagnetic flow meter in the polymer feed line for the C-Press 900-AD-03 Alarm (900-FT-06)
Utilities.ServiceWater.Signal.Pressure01 | Float | [7 empty] | Pressure gauge for indicating the level in water storage tank 1 (100-PIT-01)
Utilities.ServiceWater.Signal.Pressure02 | Float | [7 empty] | Pressure gauge for indicating the level in water storage tank 2 (100-PIT-02)
Utilities.ServiceWater.Signal.LevelSwitchLow | Float | [7 empty] | Level switch low in water storage tank 1 (100-LSL-01)
Utilities.ServiceWater.Equipment.Pump01.Run | Boolean | [7 empty] | Washing Pump for the Sludge Thickening and Dewatering System (900-BR-01) Status Run
Utilities.ServiceWater.Equipment.Pump01.Alarm | Boolean | [7 empty] | Washing Pump for the Sludge Thickening and Dewatering System (900-BR-01) Alarm
Utilities.ServiceWater.Equipment.Pump01.Mode | Boolean | [7 empty] | Washing Pump for the Sludge Thickening and Dewatering System (900-BR-01) Mode from SCADA (0=Manual, 1=Auto)
Utilities.ServiceWater.Equipment.Pump01.Frequency | Float | [7 empty] | Washing Pump for the Sludge Thickening and Dewatering System (900-BR-01) Frequency
Utilities.ServiceWater.Equipment.Pump01.Power | Float | [7 empty] | Washing Pump for the Sludge Thickening and Dewatering System (900-BR-01) Power (kW)
Utilities.ServiceWater.Equipment.Pump01.Capacity | Float | [7 empty] | Washing Pump for the Sludge Thickening and Dewatering System (900-BR-01) Capacity
Utilities.ServiceWater.Equipment.Pump02.Run | Boolean | [7 empty] | Washing Pump for the Sludge Thickening and Dewatering System (900-BR-02) Status Run
Utilities.ServiceWater.Equipment.Pump02.Alarm | Boolean | [7 empty] | Washing Pump for the Sludge Thickening and Dewatering System (900-BR-02) Alarm
Utilities.ServiceWater.Equipment.Pump02.Mode | Boolean | [7 empty] | Washing Pump for the Sludge Thickening and Dewatering System (900-BR-02) Mode from SCADA (0=Manual, 1=Auto)
Utilities.ServiceWater.Equipment.Pump02.Frequency | Float | [7 empty] | Washing Pump for the Sludge Thickening and Dewatering System (900-BR-02) Frequency
Utilities.ServiceWater.Equipment.Pump02.Power | Float | [7 empty] | Washing Pump for the Sludge Thickening and Dewatering System (900-BR-02) Power (kW)
Utilities.ServiceWater.Equipment.Pump02.Capacity | Float | [7 empty] | Washing Pump for the Sludge Thickening and Dewatering System (900-BR-02) Capacity
Utilities.ServiceWater.Equipment.Valve01.Open | Boolean | [7 empty] | Solenoid valve for controlling water intake into the suction line of the 900-BO-03 slurry pump, Open status (900-SV-01)
Utilities.ServiceWater.Equipment.Valve01.Closed | Boolean | [7 empty] | Solenoid valve for controlling water intake into the suction line of the 900-BO-03 slurry pump, Closed status (900-SV-01)
Utilities.ServiceWater.Equipment.Valve01.Alarm | Boolean | [7 empty] | Solenoid valve for controlling water intake into the suction line of the 900-BO-03 slurry pump, Alarm status (900-SV-01)
Utilities.ServiceWater.Equipment.Valve01.Mode | Boolean | [7 empty] | Solenoid valve for controlling water intake into the suction line of the 900-BO-03 slurry pump (900-SV-01) Mode from SCADA (0=Manual, 1=Auto)
Utilities.ServiceWater.Equipment.Valve02.Open | Boolean | [7 empty] | Solenoid valve for controlling water intake into the suction line of the 900-BO-02 slurry pump, Open status (900-SV-02)
Utilities.ServiceWater.Equipment.Valve02.Closed | Boolean | [7 empty] | Solenoid valve for controlling water intake into the suction line of the 900-BO-02 slurry pump, Closed status (900-SV-02)
Utilities.ServiceWater.Equipment.Valve02.Alarm | Boolean | [7 empty] | Solenoid valve for controlling water intake into the suction line of the 900-BO-02 slurry pump, Alarm status (900-SV-02)
Utilities.ServiceWater.Equipment.Valve02.Mode | Boolean | [7 empty] | Solenoid valve for controlling water intake into the suction line of the 900-BO-02 slurry pump (900-SV-02) Mode from SCADA (0=Manual, 1=Auto)
Utilities.ServiceWater.Equipment.Valve03.Open | Boolean | [7 empty] | Solenoid valve for controlling water intake into the suction line of the 900-BO-01 slurry pump, Open status (900-SV-03)
Utilities.ServiceWater.Equipment.Valve03.Closed | Boolean | [7 empty] | Solenoid valve for controlling water intake into the suction line of the 900-BO-01 slurry pump, Closed status (900-SV-03)
Utilities.ServiceWater.Equipment.Valve03.Alarm | Boolean | [7 empty] | Solenoid valve for controlling water intake into the suction line of the 900-BO-01 slurry pump, Alarm status (900-SV-03)
Utilities.ServiceWater.Equipment.Valve03.Mode | Boolean | [7 empty] | Solenoid valve for controlling water intake into the suction line of the 900-BO-01 slurry pump (900-SV-03) Mode from SCADA (0=Manual, 1=Auto)
Utilities.ServiceWater.Equipment.Valve04.Open | Boolean | [7 empty] | Solenoid valve for controlling water inlet on the C-Press 900-AD-01, Open status (900-SV-04)
Utilities.ServiceWater.Equipment.Valve04.Closed | Boolean | [7 empty] | Solenoid valve for controlling water inlet on the C-Press 900-AD-01, Closed status (900-SV-04)
Utilities.ServiceWater.Equipment.Valve04.Alarm | Boolean | [7 empty] | Solenoid valve for controlling water inlet on the C-Press 900-AD-01, Alarm status (900-SV-04)
Utilities.ServiceWater.Equipment.Valve04.Mode | Boolean | [7 empty] | Solenoid valve for controlling water inlet on the C-Press 900-AD-01 (900-SV-04) Mode from SCADA (0=Manual, 1=Auto)
Utilities.ServiceWater.Equipment.Valve05.Open | Boolean | [7 empty] | Solenoid valve for controlling water inlet on the C-Press 900-AD-02, Open status (900-SV-06)
Utilities.ServiceWater.Equipment.Valve05.Closed | Boolean | [7 empty] | Solenoid valve for controlling water inlet on the C-Press 900-AD-02, Closed status (900-SV-06)
Utilities.ServiceWater.Equipment.Valve05.Alarm | Boolean | [7 empty] | Solenoid valve for controlling water inlet on the C-Press 900-AD-02, Alarm status (900-SV-06)
Utilities.ServiceWater.Equipment.Valve05.Mode | Boolean | [7 empty] | Solenoid valve for controlling water inlet on the C-Press 900-AD-02 (900-SV-06) Mode from SCADA (0=Manual, 1=Auto)
Utilities.ServiceWater.Equipment.Valve06.Open | Boolean | [7 empty] | Solenoid valve for controlling water inlet on the C-Press 900-AD-03, Open status (900-SV-08)
Utilities.ServiceWater.Equipment.Valve06.Closed | Boolean | [7 empty] | Solenoid valve for controlling water inlet on the C-Press 900-AD-03, Closed status (900-SV-08)
Utilities.ServiceWater.Equipment.Valve06.Alarm | Boolean | [7 empty] | Solenoid valve for controlling water inlet on the C-Press 900-AD-03, Alarm status (900-SV-08)
Utilities.ServiceWater.Equipment.Valve06.Mode | Boolean | [7 empty] | Solenoid valve for controlling water inlet on the C-Press 900-AD-03 (900-SV-08) Mode from SCADA (0=Manual, 1=Auto)
FeedBuffer.Signal.LevelSwitchHighHigh | Float | [7 empty] | Level Switch high high in Feed Buffer (40-LSHH-0002)
FeedBuffer.Signal.LevelSwitchHighHigh.Alarm | Boolean | [7 empty] | Level Switch high high in Feed Buffer Alarm (40-LSHH-0002)
FeedBuffer.Signal.Conductivity | Float | [7 empty] | Conductivity Analyzer in the Suction Well of the pretrated sewage pumping station (40-QT-0004)
FeedBuffer.Signal.Conductivity.Alarm | Boolean | [7 empty] | Conductivity Analyzer in the Suction Well of the pretrated sewage pumping station Alarm (40-QT-0004)
FeedBuffer.Signal.pH | Float | [7 empty] | pH analyzer in the suction well of the pretrated sewage pumping station (40-QT-0005)
FeedBuffer.Signal.pH.Alarm | Boolean | [7 empty] | pH analyzer in the suction well of the pretrated sewage pumping station Alarm (40-QT-0005)
FeedBuffer.Signal.Turbidity | Float | [7 empty] | Turbidity analyzer in the suction well of the pretrated sewage pumping station (100-AIT-02)
FeedBuffer.Signal.Turbidity.Alarm | Boolean | [7 empty] | Turbidity analyzer in the suction well of the pretrated sewage pumping station Alarm (100-AIT-02)
FeedBuffer.Signal.FlowOut | Float | [7 empty] | Flow from Feed Buffer to Reactors 1 and 2 (40-FT-05)
FeedBuffer.Signal.FlowOut.Alarm | Boolean | [7 empty] | Flow from Feed Buffer to Reactors 1 and 2 Alarm (40-FT-05)
FeedBuffer.Equipment.Mixer01.Run | Boolean | [7 empty] | Mixer 1 in Feed Buffer (R-4005-A) Status Run
FeedBuffer.Equipment.Mixer01.Alarm | Boolean | [7 empty] | Mixer 1 in Feed Buffer (R-4005-A) Alarm
FeedBuffer.Equipment.Mixer01.Mode | Boolean | [7 empty] | Mixer 1 in Feed Buffer (R-4005-A) Mode from SCADA (0=Manual, 1=Auto)
FeedBuffer.Equipment.Mixer01.Frequency | Float | [7 empty] | Mixer 1 in Feed Buffer (R-4005-A) Frequency
FeedBuffer.Equipment.Mixer01.Power | Float | [7 empty] | Mixer 1 in Feed Buffer (R-4005-A) Power (kW)
FeedBuffer.Equipment.Mixer01.Capacity | Float | [7 empty] | Mixer 1 in Feed Buffer (R-4005-A) Capacity
FeedBuffer.Equipment.Mixer02.Run | Boolean | [7 empty] | Mixer 2 in Feed Buffer (R-4005-B) Status Run
FeedBuffer.Equipment.Mixer02.Alarm | Boolean | [7 empty] | Mixer 2 in Feed Buffer (R-4005-B) Alarm
FeedBuffer.Equipment.Mixer02.Mode | Boolean | [7 empty] | Mixer 2 in Feed Buffer (R-4005-B) Mode from SCADA (0=Manual, 1=Auto)
FeedBuffer.Equipment.Mixer02.Frequency | Float | [7 empty] | Mixer 2 in Feed Buffer (R-4005-B) Frequency
FeedBuffer.Equipment.Mixer02.Power | Float | [7 empty] | Mixer 2 in Feed Buffer (R-4005-B) Power (kW)
FeedBuffer.Equipment.Mixer02.Capacity | Float | [7 empty] | Mixer 2 in Feed Buffer (R-4005-B) Capacity
FeedBuffer.Equipment.FeedPump01.Run | Boolean | [7 empty] | Feed pump 1 to reactors (P-4001) Status Run
FeedBuffer.Equipment.FeedPump01.Alarm | Boolean | [7 empty] | Feed pump 1 to reactors (P-4001) Alarm
FeedBuffer.Equipment.FeedPump01.Mode | Boolean | [7 empty] | Feed pump 1 to reactors (P-4001) Mode from SCADA (0=Manual, 1=Auto)
FeedBuffer.Equipment.FeedPump01.Frequency | Float | [7 empty] | Feed pump 1 to reactors (P-4001) Frequency
FeedBuffer.Equipment.FeedPump01.Power | Float | [7 empty] | Feed pump 1 to reactors (P-4001) Power (kW)
FeedBuffer.Equipment.FeedPump01.Capacity | Float | [7 empty] | Feed pump 1 to reactors (P-4001) Capacity
FeedBuffer.Equipment.FeedPump02.Run | Boolean | [7 empty] | Feed pump 2 to reactors (P-4002) Status Run
FeedBuffer.Equipment.FeedPump02.Alarm | Boolean | [7 empty] | Feed pump 2 to reactors (P-4002) Alarm
FeedBuffer.Equipment.FeedPump02.Mode | Boolean | [7 empty] | Feed pump 2 to reactors (P-4002) Mode from SCADA (0=Manual, 1=Auto)
FeedBuffer.Equipment.FeedPump02.Frequency | Float | [7 empty] | Feed pump 2 to reactors (P-4002) Frequency
FeedBuffer.Equipment.FeedPump02.Power | Float | [7 empty] | Feed pump 2 to reactors (P-4002) Power (kW)
FeedBuffer.Equipment.FeedPump02.Capacity | Float | [7 empty] | Feed pump 2 to reactors (P-4002) Capacity
FeedBuffer.Equipment.FeedPump03.Run | Boolean | [7 empty] | Feed pump 3 to reactors (P-4003) Status Run
FeedBuffer.Equipment.FeedPump03.Alarm | Boolean | [7 empty] | Feed pump 3 to reactors (P-4003) Alarm
FeedBuffer.Equipment.FeedPump03.Mode | Boolean | [7 empty] | Feed pump 3 to reactors (P-4003) Mode from SCADA (0=Manual, 1=Auto)
FeedBuffer.Equipment.FeedPump03.Frequency | Float | [7 empty] | Feed pump 3 to reactors (P-4003) Frequency
FeedBuffer.Equipment.FeedPump03.Power | Float | [7 empty] | Feed pump 3 to reactors (P-4003) Power (kW)
FeedBuffer.Equipment.FeedPump03.Capacity | Float | [7 empty] | Feed pump 3 to reactors (P-4003) Capacity
FeedBuffer.Compartment.Signal.Level | Float | [7 empty] | Compartment Ultrasonic level sensor in the suction well of the pretrated sewage pumping station (40-LIT-0001)
FeedBuffer.Compartment.Signal.Level.Alarm | Boolean | [7 empty] | Compartment Ultrasonic level sensor in the suction well of the pretrated sewage pumping station Alarm (40-LIT-0001)
SludgeBuffer01.Command.Reset | Boolean | [7 empty] | SludgeBuffer01 reset command from SCADA
SludgeBuffer01.PLCMode | Boolean | [7 empty] | SludgeBuffer01 Mode from SCADA 1=Scada, 0=NC
SludgeBuffer01.Signal.Level | Float | [7 empty] | SludgeBuffer01 Level sensor in Sludge Buffer (49-LIT-0001)
SludgeBuffer01.Signal.Level.Alarm | Boolean | [7 empty] | SludgeBuffer01 Level sensor in Sludge Buffer Alarm (49-LIT-0001)
SludgeBuffer01.Signal.LevelSwitchHigh | Float | [7 empty] | SludgeBuffer01 Level switch high in Sludge Buffer (49-LSH-0002)
SludgeBuffer01.Signal.DrySolids | Float | [7 empty] | SludgeBuffer01 Suspended solids sensor after sludge discharge pumps (40-QT-0003)
SludgeBuffer01.Signal.DrySolids.Alarm | Boolean | [7 empty] | SludgeBuffer01 Suspended solids sensor after sludge discharge pumps Alarm (40-QT-0003)
SludgeBuffer01.Signal.FlowOut | Float | [7 empty] | SludgeBuffer01 Flow out after sludge discharge pumps (49-FT-0004)
SludgeBuffer01.Signal.FlowOut.Alarm | Boolean | [7 empty] | SludgeBuffer01 Flow out after sludge discharge pumps Alarm (49-FT-0004)
SludgeBuffer01.Equipment.Valve.Open | Boolean | [7 empty] | SludgeBuffer01 Control valve for Sludge, Open status (AV-49-002)
SludgeBuffer01.Equipment.Valve.Closed | Boolean | [7 empty] | SludgeBuffer01 Control valve for Sludge, Closed status (AV-49-002)
SludgeBuffer01.Equipment.Valve.Alarm | Boolean | [7 empty] | SludgeBuffer01 Control valve for Sludge, Alarm status (AV-49-002)
SludgeBuffer01.Equipment.Valve.Mode | Boolean | [7 empty] | SludgeBuffer01 Control valve for Sludge (AV-49-002) Mode from SCADA (0=Manual, 1=Auto)
SludgeBuffer01.Equipment.SludgeDischargeValve01.Open | Boolean | [7 empty] | SludgeBuffer01 Sludge discharge from SB to Influent buffer, Open status (AV-49-003)
SludgeBuffer01.Equipment.SludgeDischargeValve01.Closed | Boolean | [7 empty] | SludgeBuffer01 Sludge discharge from SB to Influent buffer, Closed status (AV-49-003)
SludgeBuffer01.Equipment.SludgeDischargeValve01.Alarm | Boolean | [7 empty] | SludgeBuffer01 Sludge discharge from SB to Influent buffer, Alarm status (AV-49-003)
SludgeBuffer01.Equipment.SludgeDischargeValve01.Mode | Boolean | [7 empty] | SludgeBuffer01 Sludge discharge from SB to Influent buffer (AV-49-003) Mode from SCADA (0=Manual, 1=Auto)
SludgeBuffer01.Equipment.SludgeDischargeValve02.Open | Boolean | [7 empty] | SludgeBuffer01 Sludge discharge from SB to Sludge storage tank1, Open status (AV-49-004)
SludgeBuffer01.Equipment.SludgeDischargeValve02.Closed | Boolean | [7 empty] | SludgeBuffer01 Sludge discharge from SB to Sludge storage tank1, Closed status (AV-49-004)
SludgeBuffer01.Equipment.SludgeDischargeValve02.Alarm | Boolean | [7 empty] | SludgeBuffer01 Sludge discharge from SB to Sludge storage tank1, Alarm status (AV-49-004)
SludgeBuffer01.Equipment.SludgeDischargeValve02.Mode | Boolean | [7 empty] | SludgeBuffer01 Sludge discharge from SB to Sludge storage tank1 (AV-49-004) Mode from SCADA (0=Manual, 1=Auto)
SludgeBuffer01.Equipment.SludgeDischargeValve03.Open | Boolean | [7 empty] | SludgeBuffer01 Sludge discharge from SB to Sludge storage tank2, Open status (AV-49-005)
SludgeBuffer01.Equipment.SludgeDischargeValve03.Closed | Boolean | [7 empty] | SludgeBuffer01 Sludge discharge from SB to Sludge storage tank2, Closed status (AV-49-005)
SludgeBuffer01.Equipment.SludgeDischargeValve03.Alarm | Boolean | [7 empty] | SludgeBuffer01 Sludge discharge from SB to Sludge storage tank2, Alarm status (AV-49-005)
SludgeBuffer01.Equipment.SludgeDischargeValve03.Mode | Boolean | [7 empty] | SludgeBuffer01 Sludge discharge from SB to Sludge storage tank2 (AV-49-005) Mode from SCADA (0=Manual, 1=Auto)
SludgeBuffer01.Equipment.SludgeDischargePump01.Run | Boolean | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 1 (P-4901) Status Run
SludgeBuffer01.Equipment.SludgeDischargePump01.Alarm | Boolean | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 1 (P-4901) Alarm
SludgeBuffer01.Equipment.SludgeDischargePump01.Mode | Boolean | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 1 (P-4901) Mode from SCADA (0=Manual, 1=Auto)
SludgeBuffer01.Equipment.SludgeDischargePump01.Frequency | Float | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 1 (P-4901) Frequency
SludgeBuffer01.Equipment.SludgeDischargePump01.Power | Float | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 1 (P-4901) Power (kW)
SludgeBuffer01.Equipment.SludgeDischargePump01.Capacity | Float | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 1 (P-4901) Capacity
SludgeBuffer01.Equipment.SludgeDischargePump02.Run | Boolean | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 2 (P-4902) Status Run
SludgeBuffer01.Equipment.SludgeDischargePump02.Alarm | Boolean | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 2 (P-4902) Alarm
SludgeBuffer01.Equipment.SludgeDischargePump02.Mode | Boolean | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 2 (P-4902) Mode from SCADA (0=Manual, 1=Auto)
SludgeBuffer01.Equipment.SludgeDischargePump02.Frequency | Float | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 2 (P-4902) Frequency
SludgeBuffer01.Equipment.SludgeDischargePump02.Power | Float | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 2 (P-4902) Power (kW)
SludgeBuffer01.Equipment.SludgeDischargePump02.Capacity | Float | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 2 (P-4902) Capacity
SludgeBuffer01.Equipment.SludgeDischargePump03.Run | Boolean | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 3 (P-4903) Status Run
SludgeBuffer01.Equipment.SludgeDischargePump03.Alarm | Boolean | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 3 (P-4903) Alarm
SludgeBuffer01.Equipment.SludgeDischargePump03.Mode | Boolean | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 3 (P-4903) Mode from SCADA (0=Manual, 1=Auto)
SludgeBuffer01.Equipment.SludgeDischargePump03.Frequency | Float | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 3 (P-4903) Frequency
SludgeBuffer01.Equipment.SludgeDischargePump03.Power | Float | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 3 (P-4903) Power (kW)
SludgeBuffer01.Equipment.SludgeDischargePump03.Capacity | Float | [7 empty] | SludgeBuffer01 Equalized sludge booster pump 3 (P-4903) Capacity
SludgeBuffer01.Phase.SB_Feed.Status | Integer | [7 empty] | SludgeBuffer01 Phase Feed Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
SludgeBuffer01.Phase.SB_Feed.OperatingConditionsFailed | Integer | [7 empty] | SludgeBuffer01 Phase Feed Operating Conditions Failed
SludgeBuffer01.Phase.SB_Wait.Status | Integer | [7 empty] | SludgeBuffer01 Phase Wait Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
SludgeBuffer01.Phase.SB_SludgeDischarge.Status | Integer | [7 empty] | SludgeBuffer01 Phase SludgeDischarge Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
SludgeBuffer01.Phase.SB_SludgeDischarge.OperatingConditionsFailed | Integer | [7 empty] | SludgeBuffer01 Phase SludgeDischarge Operating Conditions Failed
SludgeBuffer01.Phase.SB_WaterDischarge.Status | Integer | [7 empty] | SludgeBuffer01 Phase WaterDischarge Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
SludgeBuffer01.Phase.SB_WaterDischarge.OperatingConditionsFailed | Integer | [7 empty] | SludgeBuffer01 Phase WaterDischarge Operating Conditions Failed
Line01.Nereda01.Command.Reset | Boolean | [7 empty] | Line01.Nereda01 reset command from SCADA
Line01.Nereda01.PLCMode | Boolean | [7 empty] | Line01.Nereda01 Mode from SCADA 1=Scada, 0=NC
Line01.Nereda01.Equipment.FeedValve.Open | Boolean | [7 empty] | Line01.Nereda01 Feed Valve Reactor 1, Open status (AV-41-101)
Line01.Nereda01.Equipment.FeedValve.Closed | Boolean | [7 empty] | Line01.Nereda01 Feed Valve Reactor 1, Closed status (AV-41-101)
Line01.Nereda01.Equipment.FeedValve.Alarm | Boolean | [7 empty] | Line01.Nereda01 Feed Valve Reactor 1, Alarm status (AV-41-101)
Line01.Nereda01.Equipment.FeedValve.Mode | Boolean | [7 empty] | Line01.Nereda01 Feed Valve Reactor 1 (AV-41-101) Mode from SCADA (0=Manual, 1=Auto)
Line01.Nereda01.Equipment.SludgeDischargePressurizationValve.Open | Boolean | [7 empty] | Line01.Nereda01 Air fill valve Sludge Discharge for Reactor 1, Open status (AV-41-171)
Line01.Nereda01.Equipment.SludgeDischargePressurizationValve.Closed | Boolean | [7 empty] | Line01.Nereda01 Air fill valve Sludge Discharge for Reactor 1, Closed status (AV-41-171)
Line01.Nereda01.Equipment.SludgeDischargePressurizationValve.Alarm | Boolean | [7 empty] | Line01.Nereda01 Air fill valve Sludge Discharge for Reactor 1, Alarm status (AV-41-171)
Line01.Nereda01.Equipment.SludgeDischargePressurizationValve.Mode | Boolean | [7 empty] | Line01.Nereda01 Air fill valve Sludge Discharge for Reactor 1 (AV-41-171) Mode from SCADA (0=Manual, 1=Auto)
Line01.Nereda01.Equipment.SludgeDischargeVentValve.Open | Boolean | [7 empty] | Line01.Nereda01 Vent Valve Sludge Grid for Reactor 1, Open status (AV-41-172)
Line01.Nereda01.Equipment.SludgeDischargeVentValve.Closed | Boolean | [7 empty] | Line01.Nereda01 Vent Valve Sludge Grid for Reactor 1, Closed status (AV-41-172)
Line01.Nereda01.Equipment.SludgeDischargeVentValve.Alarm | Boolean | [7 empty] | Line01.Nereda01 Vent Valve Sludge Grid for Reactor 1, Alarm status (AV-41-172)
Line01.Nereda01.Equipment.SludgeDischargeVentValve.Mode | Boolean | [7 empty] | Line01.Nereda01 Vent Valve Sludge Grid for Reactor 1 (AV-41-172) Mode from SCADA (0=Manual, 1=Auto)
Line01.Nereda01.Equipment.PressureReliefValve.Open | Boolean | [7 empty] | Line01.Nereda01 Pressure Relief Valve for Reactor 1, Open status (AV-41-107)
Line01.Nereda01.Equipment.PressureReliefValve.Closed | Boolean | [7 empty] | Line01.Nereda01 Pressure Relief Valve for Reactor 1, Closed status (AV-41-107)
Line01.Nereda01.Equipment.PressureReliefValve.Alarm | Boolean | [7 empty] | Line01.Nereda01 Pressure Relief Valve for Reactor 1, Alarm status (AV-41-107)
Line01.Nereda01.Equipment.PressureReliefValve.Mode | Boolean | [7 empty] | Line01.Nereda01 Pressure Relief Valve for Reactor 1 (AV-41-107) Mode from SCADA (0=Manual, 1=Auto)
Line01.Nereda01.Equipment.LowerLevelValve.Open | Boolean | [7 empty] | Line01.Nereda01 Lower level valve Reactor 1, Open status (AV-41-102)
Line01.Nereda01.Equipment.LowerLevelValve.Closed | Boolean | [7 empty] | Line01.Nereda01 Lower level valve Reactor 1, Closed status (AV-41-102)
Line01.Nereda01.Equipment.LowerLevelValve.Alarm | Boolean | [7 empty] | Line01.Nereda01 Lower level valve Reactor 1, Alarm status (AV-41-102)
Line01.Nereda01.Equipment.LowerLevelValve.Mode | Boolean | [7 empty] | Line01.Nereda01 Lower level valve Reactor 1 (AV-41-102) Mode from SCADA (0=Manual, 1=Auto)
Line01.Nereda01.Equipment.SludgeDischargeValve.Open | Boolean | [7 empty] | Line01.Nereda01 Sludge discharge valve Reactor 1, Open status (AV-41-103)
Line01.Nereda01.Equipment.SludgeDischargeValve.Closed | Boolean | [7 empty] | Line01.Nereda01 Sludge discharge valve Reactor 1, Closed status (AV-41-103)
Line01.Nereda01.Equipment.SludgeDischargeValve.Alarm | Boolean | [7 empty] | Line01.Nereda01 Sludge discharge valve Reactor 1, Alarm status (AV-41-103)
Line01.Nereda01.Equipment.SludgeDischargeValve.Mode | Boolean | [7 empty] | Line01.Nereda01 Sludge discharge valve Reactor 1 (AV-41-103) Mode from SCADA (0=Manual, 1=Auto)
Line01.Nereda01.Equipment.AerationBlockValve.Open | Boolean | [7 empty] | Line01.Nereda01 Aeration valve for Reactor 1, Open status (AV-41-170)
Line01.Nereda01.Equipment.AerationBlockValve.Closed | Boolean | [7 empty] | Line01.Nereda01 Aeration valve for Reactor 1, Closed status (AV-41-170)
Line01.Nereda01.Equipment.AerationBlockValve.Alarm | Boolean | [7 empty] | Line01.Nereda01 Aeration valve for Reactor 1, Alarm status (AV-41-170)
Line01.Nereda01.Equipment.AerationBlockValve.Mode | Boolean | [7 empty] | Line01.Nereda01 Aeration valve for Reactor 1 (AV-41-170) Mode from SCADA (0=Manual, 1=Auto)
Line01.Nereda01.Equipment.AerationBlockValve.Position | Float | [7 empty] | Line01.Nereda01 Aeration valve for Reactor 1, Position (AV-41-170)
Line01.Nereda01.Phase.Feed.Status | Integer | [7 empty] | Line01.Nereda01 Phase Feed Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
Line01.Nereda01.Phase.Feed.OperatingConditionsFailed | Integer | [7 empty] | Line01.Nereda01 Phase Feed Operating Conditions Failed
Line01.Nereda01.Phase.LowerLevel.Status | Integer | [7 empty] | Line01.Nereda01 Phase LowerLevel Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
Line01.Nereda01.Phase.LowerLevel.OperatingConditionsFailed | Integer | [7 empty] | Line01.Nereda01 Phase LowerLevel Operating Conditions Failed
Line01.Nereda01.Phase.Aerate.Status | Integer | [7 empty] | Line01.Nereda01 Phase Aerate Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
Line01.Nereda01.Phase.Aerate.OperatingConditionsFailed | Integer | [7 empty] | Line01.Nereda01 Phase Aerate Operating Conditions Failed
Line01.Nereda01.Phase.MetalDosingFeed.Status | Integer | [7 empty] | Line01.Nereda01 Phase MetalDosingFeed Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
Line01.Nereda01.Phase.MetalDosingFeed.OperatingConditionsFailed | Integer | [7 empty] | Line01.Nereda01 Phase MetalDosingFeed Operating Conditions Failed
Line01.Nereda01.Phase.Wait.Status | Integer | [7 empty] | Line01.Nereda01 Phase Wait Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
Line01.Nereda01.Phase.Discharge.Status | Integer | [7 empty] | Line01.Nereda01 Phase Discharge Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
Line01.Nereda01.Phase.Discharge.OperatingConditionsFailed | Integer | [7 empty] | Line01.Nereda01 Phase Discharge Operating Conditions Failed
Line01.Nereda01.Phase.VentAirGrid.Status | Integer | [7 empty] | Line01.Nereda01 Phase VentAirGrid Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
Line01.Nereda01.Phase.VentAirGrid.OperatingConditionsFailed | Integer | [7 empty] | Line01.Nereda01 Phase VentAirGrid Operating Conditions Failed
Line01.Nereda01.Phase.VentSludgeGrid.Status | Integer | [7 empty] | Line01.Nereda01 Phase VentSludgeGrid Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
Line01.Nereda01.Phase.VentSludgeGrid.OperatingConditionsFailed | Integer | [7 empty] | Line01.Nereda01 Phase VentSludgeGrid Operating Conditions Failed
Line01.Nereda01.Signal.Level | Float | [7 empty] | Line01.Nereda01 Level in Reactor 1 (41-LT-1005)
Line01.Nereda01.Signal.Level.Alarm | Boolean | [7 empty] | Line01.Nereda01 Level in Reactor 1 Alarm (41-LT-1005)
Line01.Nereda01.Signal.O2 | Float | [7 empty] | Line01.Nereda01 O2 in Reactor 1 (41-QT-1002)
Line01.Nereda01.Signal.O2.CommonError | Boolean | [7 empty] | Line01.Nereda01 O2 in Reactor 1 CommonError bit from 16-bit analyzer status word, Bit 3 (41-QT-1002)
Line01.Nereda01.Signal.O2.Reliability | Float | [7 empty] | Line01.Nereda01 O2 in Reactor 1 Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (41-QT-1002)
Line01.Nereda01.Signal.O2.DaysToMaintenance | Integer | [7 empty] | Line01.Nereda01 O2 in Reactor 1 DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (41-QT-1002)
Line01.Nereda01.Signal.Temperature | Float | [7 empty] | Line01.Nereda01 Temperature in Reactor 1 (41-QT-1003)
Line01.Nereda01.Signal.Temperature.CommonError | Boolean | [7 empty] | Line01.Nereda01 Temperature in Reactor 1 CommonError bit from 16-bit analyzer status word, Bit 3 (41-QT-1003)
Line01.Nereda01.Signal.Temperature.Reliability | Float | [7 empty] | Line01.Nereda01 Temperature in Reactor 1 Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (41-QT-1003)
Line01.Nereda01.Signal.Temperature.DaysToMaintenance | Integer | [7 empty] | Line01.Nereda01 Temperature in Reactor 1 DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (41-QT-1003)
Line01.Nereda01.Signal.Redox | Float | [7 empty] | Line01.Nereda01 ORP sensor Reactor 1 (41-QT-1004)
Line01.Nereda01.Signal.Redox.CommonError | Boolean | [7 empty] | Line01.Nereda01 ORP sensor Reactor 1 CommonError bit from 16-bit analyzer status word, Bit 3 (41-QT-1004)
Line01.Nereda01.Signal.Redox.Reliability | Float | [7 empty] | Line01.Nereda01 ORP sensor Reactor 1 Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (41-QT-1004)
Line01.Nereda01.Signal.Redox.DaysToMaintenance | Integer | [7 empty] | Line01.Nereda01 ORP sensor Reactor 1 DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (41-QT-1004)
Line01.Nereda01.Signal.NH4 | Float | [7 empty] | Line01.Nereda01 NH4 sensor Reactor 1 (41-QT-1007)
Line01.Nereda01.Signal.NH4.CommonError | Boolean | [7 empty] | Line01.Nereda01 NH4 sensor Reactor 1 CommonError bit from 16-bit analyzer status word, Bit 3 (41-QT-1007)
Line01.Nereda01.Signal.NH4.Reliability | Float | [7 empty] | Line01.Nereda01 NH4 sensor Reactor 1 Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (41-QT-1007)
Line01.Nereda01.Signal.NH4.DaysToMaintenance | Integer | [7 empty] | Line01.Nereda01 NH4 sensor Reactor 1 DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (41-QT-1007)
Line01.Nereda01.Signal.NO3 | Float | [7 empty] | Line01.Nereda01 NO3 sensor Reactor 1 (41-QT-1008)
Line01.Nereda01.Signal.NO3.CommonError | Boolean | [7 empty] | Line01.Nereda01 NO3 sensor Reactor 1 CommonError bit from 16-bit analyzer status word, Bit 3 (41-QT-1008)
Line01.Nereda01.Signal.NO3.Reliability | Float | [7 empty] | Line01.Nereda01 NO3 sensor Reactor 1 Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (41-QT-1008)
Line01.Nereda01.Signal.NO3.DaysToMaintenance | Integer | [7 empty] | Line01.Nereda01 NO3 sensor Reactor 1 DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (41-QT-1008)
Line01.Nereda01.Signal.PO4 | Float | [7 empty] | Line01.Nereda01 PO4 sensor Reactor 1 (41-QT-1009)
Line01.Nereda01.Signal.PO4.CommonError | Boolean | [7 empty] | Line01.Nereda01 PO4 sensor Reactor 1 CommonError bit from 16-bit analyzer status word, Bit 3 (41-QT-1009)
Line01.Nereda01.Signal.PO4.Reliability | Float | [7 empty] | Line01.Nereda01 PO4 sensor Reactor 1 Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (41-QT-1009)
Line01.Nereda01.Signal.PO4.DaysToMaintenance | Integer | [7 empty] | Line01.Nereda01 PO4 sensor Reactor 1 DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (41-QT-1009)
Line01.Nereda01.Signal.DrySolids | Float | [7 empty] | Line01.Nereda01 Suspended Solids Analyzer in the Reactor 1 (41-QT-1001)
Line01.Nereda01.Signal.DrySolids.CommonError | Boolean | [7 empty] | Line01.Nereda01 Suspended Solids Analyzer in the Reactor 1 CommonError bit from 16-bit analyzer status word, Bit 3 (41-QT-1001)
Line01.Nereda01.Signal.DrySolids.Reliability | Float | [7 empty] | Line01.Nereda01 Suspended Solids Analyzer in the Reactor 1 Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (41-QT-1001)
Line01.Nereda01.Signal.DrySolids.DaysToMaintenance | Integer | [7 empty] | Line01.Nereda01 Suspended Solids Analyzer in the Reactor 1 DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (41-QT-1001)
Line01.Nereda02.Command.Reset | Boolean | [7 empty] | Line01.Nereda02 reset command from SCADA
Line01.Nereda02.PLCMode | Boolean | [7 empty] | Line01.Nereda02 Mode from SCADA 1=Scada, 0=NC
Line01.Nereda02.Equipment.FeedValve.Open | Boolean | [7 empty] | Line01.Nereda02 Feed Valve Reactor 2, Open status (AV-42-101)
Line01.Nereda02.Equipment.FeedValve.Closed | Boolean | [7 empty] | Line01.Nereda02 Feed Valve Reactor 2, Closed status (AV-42-101)
Line01.Nereda02.Equipment.FeedValve.Alarm | Boolean | [7 empty] | Line01.Nereda02 Feed Valve Reactor 2, Alarm status (AV-42-101)
Line01.Nereda02.Equipment.FeedValve.Mode | Boolean | [7 empty] | Line01.Nereda02 Feed Valve Reactor 2 (AV-42-101) Mode from SCADA (0=Manual, 1=Auto)
Line01.Nereda02.Equipment.SludgeDischargePressurizationValve.Open | Boolean | [7 empty] | Line01.Nereda02 Air fill valve Sludge Discharge for Reactor 2, Open status (AV-42-171)
Line01.Nereda02.Equipment.SludgeDischargePressurizationValve.Closed | Boolean | [7 empty] | Line01.Nereda02 Air fill valve Sludge Discharge for Reactor 2, Closed status (AV-42-171)
Line01.Nereda02.Equipment.SludgeDischargePressurizationValve.Alarm | Boolean | [7 empty] | Line01.Nereda02 Air fill valve Sludge Discharge for Reactor 2, Alarm status (AV-42-171)
Line01.Nereda02.Equipment.SludgeDischargePressurizationValve.Mode | Boolean | [7 empty] | Line01.Nereda02 Air fill valve Sludge Discharge for Reactor 2 (AV-42-171) Mode from SCADA (0=Manual, 1=Auto)
Line01.Nereda02.Equipment.SludgeDischargeVentValve.Open | Boolean | [7 empty] | Line01.Nereda02 Vent Valve Sludge Grid for Reactor 2, Open status (AV-42-172)
Line01.Nereda02.Equipment.SludgeDischargeVentValve.Closed | Boolean | [7 empty] | Line01.Nereda02 Vent Valve Sludge Grid for Reactor 2, Closed status (AV-42-172)
Line01.Nereda02.Equipment.SludgeDischargeVentValve.Alarm | Boolean | [7 empty] | Line01.Nereda02 Vent Valve Sludge Grid for Reactor 2, Alarm status (AV-42-172)
Line01.Nereda02.Equipment.SludgeDischargeVentValve.Mode | Boolean | [7 empty] | Line01.Nereda02 Vent Valve Sludge Grid for Reactor 2 (AV-42-172) Mode from SCADA (0=Manual, 1=Auto)
Line01.Nereda02.Equipment.PressureReliefValve.Open | Boolean | [7 empty] | Line01.Nereda02 Pressure Relief Valve for Reactor 2, Open status (AV-42-107)
Line01.Nereda02.Equipment.PressureReliefValve.Closed | Boolean | [7 empty] | Line01.Nereda02 Pressure Relief Valve for Reactor 2, Closed status (AV-42-107)
Line01.Nereda02.Equipment.PressureReliefValve.Alarm | Boolean | [7 empty] | Line01.Nereda02 Pressure Relief Valve for Reactor 2, Alarm status (AV-42-107)
Line01.Nereda02.Equipment.PressureReliefValve.Mode | Boolean | [7 empty] | Line01.Nereda02 Pressure Relief Valve for Reactor 2 (AV-42-107) Mode from SCADA (0=Manual, 1=Auto)
Line01.Nereda02.Equipment.LowerLevelValve.Open | Boolean | [7 empty] | Line01.Nereda02 Lower level valve Reactor 2, Open status (AV-42-102)
Line01.Nereda02.Equipment.LowerLevelValve.Closed | Boolean | [7 empty] | Line01.Nereda02 Lower level valve Reactor 2, Closed status (AV-42-102)
Line01.Nereda02.Equipment.LowerLevelValve.Alarm | Boolean | [7 empty] | Line01.Nereda02 Lower level valve Reactor 2, Alarm status (AV-42-102)
Line01.Nereda02.Equipment.LowerLevelValve.Mode | Boolean | [7 empty] | Line01.Nereda02 Lower level valve Reactor 2 (AV-42-102) Mode from SCADA (0=Manual, 1=Auto)
Line01.Nereda02.Equipment.SludgeDischargeValve.Open | Boolean | [7 empty] | Line01.Nereda02 Sludge discharge valve Reactor 2, Open status (AV-42-103)
Line01.Nereda02.Equipment.SludgeDischargeValve.Closed | Boolean | [7 empty] | Line01.Nereda02 Sludge discharge valve Reactor 2, Closed status (AV-42-103)
Line01.Nereda02.Equipment.SludgeDischargeValve.Alarm | Boolean | [7 empty] | Line01.Nereda02 Sludge discharge valve Reactor 2, Alarm status (AV-42-103)
Line01.Nereda02.Equipment.SludgeDischargeValve.Mode | Boolean | [7 empty] | Line01.Nereda02 Sludge discharge valve Reactor 2 (AV-42-103) Mode from SCADA (0=Manual, 1=Auto)
Line01.Nereda02.Equipment.AerationBlockValve.Open | Boolean | [7 empty] | Line01.Nereda02 Aeration valve for Reactor 2, Open status (AV-42-170)
Line01.Nereda02.Equipment.AerationBlockValve.Closed | Boolean | [7 empty] | Line01.Nereda02 Aeration valve for Reactor 2, Closed status (AV-42-170)
Line01.Nereda02.Equipment.AerationBlockValve.Alarm | Boolean | [7 empty] | Line01.Nereda02 Aeration valve for Reactor 2, Alarm status (AV-42-170)
Line01.Nereda02.Equipment.AerationBlockValve.Mode | Boolean | [7 empty] | Line01.Nereda02 Aeration valve for Reactor 2 (AV-42-170) Mode from SCADA (0=Manual, 1=Auto)
Line01.Nereda02.Equipment.AerationBlockValve.Position | Float | [7 empty] | Line01.Nereda02 Aeration valve for Reactor 2, Position (AV-42-170)
Line01.Nereda02.Phase.Feed.Status | Integer | [7 empty] | Line01.Nereda02 Phase Feed Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
Line01.Nereda02.Phase.Feed.OperatingConditionsFailed | Integer | [7 empty] | Line01.Nereda02 Phase Feed Operating Conditions Failed
Line01.Nereda02.Phase.LowerLevel.Status | Integer | [7 empty] | Line01.Nereda02 Phase LowerLevel Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
Line01.Nereda02.Phase.LowerLevel.OperatingConditionsFailed | Integer | [7 empty] | Line01.Nereda02 Phase LowerLevel Operating Conditions Failed
Line01.Nereda02.Phase.Aerate.Status | Integer | [7 empty] | Line01.Nereda02 Phase Aerate Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
Line01.Nereda02.Phase.Aerate.OperatingConditionsFailed | Integer | [7 empty] | Line01.Nereda02 Phase Aerate Operating Conditions Failed
Line01.Nereda02.Phase.MetalDosingFeed.Status | Integer | [7 empty] | Line01.Nereda02 Phase MetalDosingFeed Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
Line01.Nereda02.Phase.MetalDosingFeed.OperatingConditionsFailed | Integer | [7 empty] | Line01.Nereda02 Phase MetalDosingFeed Operating Conditions Failed
Line01.Nereda02.Phase.Wait.Status | Integer | [7 empty] | Line01.Nereda02 Phase Wait Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
Line01.Nereda02.Phase.Discharge.Status | Integer | [7 empty] | Line01.Nereda02 Phase Discharge Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
Line01.Nereda02.Phase.Discharge.OperatingConditionsFailed | Integer | [7 empty] | Line01.Nereda02 Phase Discharge Operating Conditions Failed
Line01.Nereda02.Phase.VentAirGrid.Status | Integer | [7 empty] | Line01.Nereda02 Phase VentAirGrid Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
Line01.Nereda02.Phase.VentAirGrid.OperatingConditionsFailed | Integer | [7 empty] | Line01.Nereda02 Phase VentAirGrid Operating Conditions Failed
Line01.Nereda02.Phase.VentSludgeGrid.Status | Integer | [7 empty] | Line01.Nereda02 Phase VentSludgeGrid Status ¦ 0=Ready, 1=Starting, 2=Run, 3=Stopping, 5=Aborting, 6=Aborted, 7=Interlocked
Line01.Nereda02.Phase.VentSludgeGrid.OperatingConditionsFailed | Integer | [7 empty] | Line01.Nereda02 Phase VentSludgeGrid Operating Conditions Failed
Line01.Nereda02.Signal.Level | Float | [7 empty] | Line01.Nereda02 Level in Reactor 2 (42-LT-1005)
Line01.Nereda02.Signal.Level.Alarm | Boolean | [7 empty] | Line01.Nereda02 Level in Reactor 2 Alarm (42-LT-1005)
Line01.Nereda02.Signal.Temperature | Float | [7 empty] | Line01.Nereda02 Temperature in Reactor 2 (42-QT-1003)
Line01.Nereda02.Signal.Temperature.CommonError | Boolean | [7 empty] | Line01.Nereda02 Temperature in Reactor 2 CommonError bit from 16-bit analyzer status word, Bit 3 (42-QT-1003)
Line01.Nereda02.Signal.Temperature.Reliability | Float | [7 empty] | Line01.Nereda02 Temperature in Reactor 2 Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (42-QT-1003)
Line01.Nereda02.Signal.Temperature.DaysToMaintenance | Integer | [7 empty] | Line01.Nereda02 Temperature in Reactor 2 DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (42-QT-1003)
Line01.Nereda02.Signal.O2 | Float | [7 empty] | Line01.Nereda02 O2 in Reactor 2 (42-QT-1002)
Line01.Nereda02.Signal.O2.CommonError | Boolean | [7 empty] | Line01.Nereda02 O2 in Reactor 2 CommonError bit from 16-bit analyzer status word, Bit 3 (42-QT-1002)
Line01.Nereda02.Signal.O2.Reliability | Float | [7 empty] | Line01.Nereda02 O2 in Reactor 2 Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (42-QT-1002)
Line01.Nereda02.Signal.O2.DaysToMaintenance | Integer | [7 empty] | Line01.Nereda02 O2 in Reactor 2 DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (42-QT-1002)
Line01.Nereda02.Signal.Redox | Float | [7 empty] | Line01.Nereda02 ORP sensor Reactor 2 (41-QT-1004)
Line01.Nereda02.Signal.Redox.CommonError | Boolean | [7 empty] | Line01.Nereda02 ORP sensor Reactor 2 CommonError bit from 16-bit analyzer status word, Bit 3 (41-QT-1004)
Line01.Nereda02.Signal.Redox.Reliability | Float | [7 empty] | Line01.Nereda02 ORP sensor Reactor 2 Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (41-QT-1004)
Line01.Nereda02.Signal.Redox.DaysToMaintenance | Integer | [7 empty] | Line01.Nereda02 ORP sensor Reactor 2 DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (41-QT-1004)
Line01.Nereda02.Signal.NH4 | Float | [7 empty] | Line01.Nereda02 NH4 sensor Reactor 2 (42-QT-1007)
Line01.Nereda02.Signal.NH4.CommonError | Boolean | [7 empty] | Line01.Nereda02 NH4 sensor Reactor 2 CommonError bit from 16-bit analyzer status word, Bit 3 (42-QT-1007)
Line01.Nereda02.Signal.NH4.Reliability | Float | [7 empty] | Line01.Nereda02 NH4 sensor Reactor 2 Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (42-QT-1007)
Line01.Nereda02.Signal.NH4.DaysToMaintenance | Integer | [7 empty] | Line01.Nereda02 NH4 sensor Reactor 2 DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (42-QT-1007)
Line01.Nereda02.Signal.NO3 | Float | [7 empty] | Line01.Nereda02 NO3 sensor Reactor 2 (42-QT-1008)
Line01.Nereda02.Signal.NO3.CommonError | Boolean | [7 empty] | Line01.Nereda02 NO3 sensor Reactor 2 CommonError bit from 16-bit analyzer status word, Bit 3 (42-QT-1008)
Line01.Nereda02.Signal.NO3.Reliability | Float | [7 empty] | Line01.Nereda02 NO3 sensor Reactor 2 Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (42-QT-1008)
Line01.Nereda02.Signal.NO3.DaysToMaintenance | Integer | [7 empty] | Line01.Nereda02 NO3 sensor Reactor 2 DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (42-QT-1008)
Line01.Nereda02.Signal.PO4 | Float | [7 empty] | Line01.Nereda02 PO4 sensor Reactor 2 (42-QT-1009)
Line01.Nereda02.Signal.PO4.CommonError | Boolean | [7 empty] | Line01.Nereda02 PO4 sensor Reactor 2 CommonError bit from 16-bit analyzer status word, Bit 3 (42-QT-1009)
Line01.Nereda02.Signal.PO4.Reliability | Float | [7 empty] | Line01.Nereda02 PO4 sensor Reactor 2 Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (42-QT-1009)
Line01.Nereda02.Signal.PO4.DaysToMaintenance | Integer | [7 empty] | Line01.Nereda02 PO4 sensor Reactor 2 DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (42-QT-1009)
Line01.Nereda02.Signal.DrySolids | Float | [7 empty] | Line01.Nereda02 Suspended Solids Analyzer in the Reactor 2 (42-QT-1001)
Line01.Nereda02.Signal.DrySolids.CommonError | Boolean | [7 empty] | Line01.Nereda02 Suspended Solids Analyzer in the Reactor 2 CommonError bit from 16-bit analyzer status word, Bit 3 (42-QT-1001)
Line01.Nereda02.Signal.DrySolids.Reliability | Float | [7 empty] | Line01.Nereda02 Suspended Solids Analyzer in the Reactor 2 Reliability signal from Hach-Lange Prognosys module, an extension to the SC-1000 (42-QT-1001)
Line01.Nereda02.Signal.DrySolids.DaysToMaintenance | Integer | [7 empty] | Line01.Nereda02 Suspended Solids Analyzer in the Reactor 2 DaysToMaintenance signal from Hach-Lange Prognosys module, an extension to the SC-1000 (42-QT-1001)

## ToPLC
Nereda Tijuco Preto | Remarks
Interface list with signals that the Nereda controller writes to the PLC
BE1364
Version V2 31/07/2026 15:59:29
Signals to PLC | DataType | Address/ Register/ TagName | Bit | Db | Scaling | Offset | Description
SludgeBuffer01.Status | Integer | [5 empty] | SludgeBuffer01 status for display on SCADA
SludgeBuffer01.Phase.SB_Feed.Command.Start | Boolean | [5 empty] | SludgeBuffer01 Phase Feed Start command from Nereda Controller
SludgeBuffer01.Phase.SB_Feed.Command.Stop | Boolean | [5 empty] | SludgeBuffer01 Phase Feed Stop command from Nereda Controller
SludgeBuffer01.Phase.SB_Wait.Command.Start | Boolean | [5 empty] | SludgeBuffer01 Phase Wait Start command from Nereda Controller
SludgeBuffer01.Phase.SB_Wait.Command.Stop | Boolean | [5 empty] | SludgeBuffer01 Phase Wait Stop command from Nereda Controller
SludgeBuffer01.Phase.SB_SludgeDischarge.Command.Start | Boolean | [5 empty] | SludgeBuffer01 Phase SludgeDischarge Start command from Nereda Controller
SludgeBuffer01.Phase.SB_SludgeDischarge.Command.Stop | Boolean | [5 empty] | SludgeBuffer01 Phase SludgeDischarge Stop command from Nereda Controller
SludgeBuffer01.Phase.SB_WaterDischarge.Command.Start | Boolean | [5 empty] | SludgeBuffer01 Phase WaterDischarge Start command from Nereda Controller
SludgeBuffer01.Phase.SB_WaterDischarge.Command.Stop | Boolean | [5 empty] | SludgeBuffer01 Phase WaterDischarge Stop command from Nereda Controller
SludgeBuffer01.Phase.SB_WaterDischarge.Control.FlowSetpoint | Float | [5 empty] | SludgeBuffer01 Phase water discharge flow setpoint ()
SludgeBuffer01.Phase.SB_SludgeDischarge.Control.FlowSetpoint | Float | [5 empty] | SludgeBuffer01 Phase sludge discharge flow setpoint ()
Line01.Nereda01.Status | Integer | [5 empty] | Line01.Nereda01 status for display on SCADA
Line01.Nereda01.Phase.Feed.Command.Start | Boolean | [5 empty] | Line01.Nereda01 Phase Feed Start command from Nereda Controller
Line01.Nereda01.Phase.Feed.Command.Stop | Boolean | [5 empty] | Line01.Nereda01 Phase Feed Stop command from Nereda Controller
Line01.Nereda01.Phase.LowerLevel.Command.Start | Boolean | [5 empty] | Line01.Nereda01 Phase LowerLevel Start command from Nereda Controller
Line01.Nereda01.Phase.LowerLevel.Command.Stop | Boolean | [5 empty] | Line01.Nereda01 Phase LowerLevel Stop command from Nereda Controller
Line01.Nereda01.Phase.Aerate.Command.Start | Boolean | [5 empty] | Line01.Nereda01 Phase Aerate Start command from Nereda Controller
Line01.Nereda01.Phase.Aerate.Command.Stop | Boolean | [5 empty] | Line01.Nereda01 Phase Aerate Stop command from Nereda Controller
Line01.Nereda01.Phase.MetalDosingFeed.Command.Start | Boolean | [5 empty] | Line01.Nereda01 Phase MetalDosingFeed Start command from Nereda Controller
Line01.Nereda01.Phase.MetalDosingFeed.Command.Stop | Boolean | [5 empty] | Line01.Nereda01 Phase MetalDosingFeed Stop command from Nereda Controller
Line01.Nereda01.Phase.Wait.Command.Start | Boolean | [5 empty] | Line01.Nereda01 Phase Wait Start command from Nereda Controller
Line01.Nereda01.Phase.Wait.Command.Stop | Boolean | [5 empty] | Line01.Nereda01 Phase Wait Stop command from Nereda Controller
Line01.Nereda01.Phase.Discharge.Command.Start | Boolean | [5 empty] | Line01.Nereda01 Phase Discharge Start command from Nereda Controller
Line01.Nereda01.Phase.Discharge.Command.Stop | Boolean | [5 empty] | Line01.Nereda01 Phase Discharge Stop command from Nereda Controller
Line01.Nereda01.Phase.VentAirGrid.Command.Start | Boolean | [5 empty] | Line01.Nereda01 Phase VentAirGrid Start command from Nereda Controller
Line01.Nereda01.Phase.VentAirGrid.Command.Stop | Boolean | [5 empty] | Line01.Nereda01 Phase VentAirGrid Stop command from Nereda Controller
Line01.Nereda01.Phase.VentSludgeGrid.Command.Start | Boolean | [5 empty] | Line01.Nereda01 Phase VentSludgeGrid Start command from Nereda Controller
Line01.Nereda01.Phase.VentSludgeGrid.Command.Stop | Boolean | [5 empty] | Line01.Nereda01 Phase VentSludgeGrid Stop command from Nereda Controller
Line01.Nereda01.Phase.Aerate.Control.PressurizeSludgeDischarge | Boolean | [5 empty] | Line01.Nereda01 Command to open air valve (AV-41-171) to sludge discharge internal in the reactor
Line01.Nereda01.Phase.Aerate.Control.Capacity | Float | [5 empty] | Line01.Nereda01 Required aeration capacity (0..100%)
Line01.Nereda01.Phase.Feed.Control.FlowSetpoint | Float | [5 empty] | Line01.Nereda01 feed flow setpoint
Line01.Nereda01.Phase.MetalDosingFeed.Control.Capacity | Float | [5 empty] | Line01.Nereda01 required MetalDosingFeed capacity (0..100%)
Line01.Nereda02.Status | Integer | [5 empty] | Line01.Nereda02 status for display on SCADA
Line01.Nereda02.Phase.Feed.Command.Start | Boolean | [5 empty] | Line01.Nereda02 Phase Feed Start command from Nereda Controller
Line01.Nereda02.Phase.Feed.Command.Stop | Boolean | [5 empty] | Line01.Nereda02 Phase Feed Stop command from Nereda Controller
Line01.Nereda02.Phase.LowerLevel.Command.Start | Boolean | [5 empty] | Line01.Nereda02 Phase LowerLevel Start command from Nereda Controller
Line01.Nereda02.Phase.LowerLevel.Command.Stop | Boolean | [5 empty] | Line01.Nereda02 Phase LowerLevel Stop command from Nereda Controller
Line01.Nereda02.Phase.Aerate.Command.Start | Boolean | [5 empty] | Line01.Nereda02 Phase Aerate Start command from Nereda Controller
Line01.Nereda02.Phase.Aerate.Command.Stop | Boolean | [5 empty] | Line01.Nereda02 Phase Aerate Stop command from Nereda Controller
Line01.Nereda02.Phase.MetalDosingFeed.Command.Start | Boolean | [5 empty] | Line01.Nereda02 Phase MetalDosingFeed Start command from Nereda Controller
Line01.Nereda02.Phase.MetalDosingFeed.Command.Stop | Boolean | [5 empty] | Line01.Nereda02 Phase MetalDosingFeed Stop command from Nereda Controller
Line01.Nereda02.Phase.Wait.Command.Start | Boolean | [5 empty] | Line01.Nereda02 Phase Wait Start command from Nereda Controller
Line01.Nereda02.Phase.Wait.Command.Stop | Boolean | [5 empty] | Line01.Nereda02 Phase Wait Stop command from Nereda Controller
Line01.Nereda02.Phase.Discharge.Command.Start | Boolean | [5 empty] | Line01.Nereda02 Phase Discharge Start command from Nereda Controller
Line01.Nereda02.Phase.Discharge.Command.Stop | Boolean | [5 empty] | Line01.Nereda02 Phase Discharge Stop command from Nereda Controller
Line01.Nereda02.Phase.VentAirGrid.Command.Start | Boolean | [5 empty] | Line01.Nereda02 Phase VentAirGrid Start command from Nereda Controller
Line01.Nereda02.Phase.VentAirGrid.Command.Stop | Boolean | [5 empty] | Line01.Nereda02 Phase VentAirGrid Stop command from Nereda Controller
Line01.Nereda02.Phase.VentSludgeGrid.Command.Start | Boolean | [5 empty] | Line01.Nereda02 Phase VentSludgeGrid Start command from Nereda Controller
Line01.Nereda02.Phase.VentSludgeGrid.Command.Stop | Boolean | [5 empty] | Line01.Nereda02 Phase VentSludgeGrid Stop command from Nereda Controller
Line01.Nereda02.Phase.Aerate.Control.PressurizeSludgeDischarge | Boolean | [5 empty] | Line01.Nereda02 Command to open air valve (AV-42-171) to sludge discharge internal in the reactor
Line01.Nereda02.Phase.Aerate.Control.Capacity | Float | [5 empty] | Line01.Nereda02 Required aeration capacity (0..100%)
Line01.Nereda02.Phase.Feed.Control.FlowSetpoint | Float | [5 empty] | Line01.Nereda02 feed flow setpoint
Line01.Nereda02.Phase.MetalDosingFeed.Control.Capacity | Float | [5 empty] | Line01.Nereda02 required MetalDosingFeed capacity (0..100%)
HeartBeat | Boolean | [5 empty] | Heartbeat signal from Nereda Controller to PLC